## Instructions
EA Prerequisite 2: Minimum Energy Performance - Table 1.4
INSTRUCTIONS
ENABLE MACROS BEFORE FILLING IN THE SPREADSHEET! (Note: Macros must be enabled each time the spreadsheet is re-opened in order to make changes to the spreadsheet)
Purpose for the Revised Section 1.4 Spreadsheet inputs: The following input sheets are intended to assist energy modelers in developing the ASHRAE 90.1 Appendix G building energy models. The inputs include specific information about the Baseline and Proposed Case ASHRAE 90.1-2007 Appendix G modeling requirements, and provide the energy modeler with input quality control checks for the energy modeling inputs. These sheets provide the greatest value to the project team if they are completed in advance of the energy model, are reviewed by the architect(s) and engineer(s) to confirm that the proposed case inputs are consistent with the actual building design, and then are used as a tool to complete the energy model inputs. Prior to LEED submission, the energy modeler should confirm that the energy model inputs listed are consistent with those modeled, and provide quality control (QC) to confirm that the outputs are reasonable based on the energy inputs listed. Note: If the energy modeler waits to fill out the spreadsheet until after the Construction Documents model has been completed, the modeler may discover some ASHRAE 90.1 modeling requirements described in this spreadsheet that were overlooked during the modeling process, and additional time may be required to revise the model. Many of the QC checks of the energy model inputs that are performed by the LEED Reviewers are embedded in these inputs sheets. Therefore, when these spreadsheet inputs are used by an experienced energy modeling professional as a tool for completing and quality checking the energy model, it is expected that the number of LEED Review comments related to the building energy model inputs at the preliminary LEED review phase will be significantly reduced.
1. Opaque Envelope Sheet
Complete the Opaque Building Envelope Requirements section, then describe each unique opaque building envelope construction on a separate row in the Opaque Building Envelope Constructions table (required inputs are green). Note that extra rows can be added using the button to the lower left of each construction type as necessary.
2. Shading & Fenestration
Provide the requested shading and orientation information (required inputs are green). Then describe each unique fenestration assembly on a separate row in the Fenestration Table.
3. Lighting Sheet
| a. | Interior lighting: Select either the Building Area Method, or the Space-by-Space Method.
(1) If using the building area method, identify each major building function within the building, and the associated square footage. Confirm the baseline lighting power density is modeled as shown for each building function, and input the proposed installed lighting power density, any automated lighting controls modeled for credit, and the revised lighting power density after any automated lighting control credits from Section G3.2.
(2) If using the space-by-space method, identify each space type within the building, and the associated square footage. Confirm the baseline lighting power density is modeled as shown for each space type and input the proposed installed lighting power density, any automated lighting controls modeled for credit, and the revised lighting power density after any automated lighting control credits from Section G3.2. Also, identify any spaces with additional lighting power allowances, and input the actual installed lighting power density for these spaces.
b. |  | Exterior Lighting: Identify whether the building has tradable or non-tradable surfaces, and enter the exterior lighting for each surface.
4. Equipment Sheet
Select the method used to model receptacle equipment, and then complete the corresponding receptacle equipment table (required inputs are green). Other process equipment should be reported in the bottom table.
5. Service Water Heating Sheet
Complete the Service Water Heaters tables for each unique type of system in the project (required inputs are green). Use the Add a System Type button for more than one type of system. Complete the Service Hot Water Fixtures table if credit is modeled for low-flow fixtures in the Proposed case. If the project includes service hot water circulation pumps, complete the Service Hot Water Pumps table.
6. General HVAC Sheet
Complete the Special Circumstances section, the Proposed and Baseline HVAC System Type(s) tables, and the HVAC Modeling Requirements checklist.
7. Air-Side HVAC Details Sheet
Enter all applicable input parameters for the Proposed air-side HVAC systems. All systems included in the model should be entered. Each individual system may be entered separately, or multiple systems may be grouped together if all input parameters identified with an (*) are similar. The table is set up for two unique HVAC systems (or two groups of similar systems), and additional systems (or groups of similar systems) should be added as necessary using the Add a System button.
8. Water-Side HVAC Details Sheet
Enter all applicable input parameters for the Baseline and Proposed water-side HVAC systems. All systems included in the model should be entered. Please refer to the Helpful Notes for information about Appendix G modeling protocol.
FAQ Regarding the Section 1.4 Spreadsheet Inputs:
Question: Can the original Table 1.4 spreadsheet still be used for LEED submissions? Answer: Yes, the original Table 1.4 spreadsheet, which consists of a single sheet, with limited space available for the opaque envelope constructions, and lighting power densities may still be used to document EAp2/EAc1 LEED compliance for all projects registered through the end of March, 2013. However, as described above, the revised Table 1.4 spreadsheet inputs are intended to assist in the energy modeling process, and assist the project team in energy model quality control prior to submitting the project for review; therefore, project teams are encouraged to make use of these new Table 1.4 spreadsheet inputs, as it is expected that this will facilitate a more streamlined review process.
Question: If the energy simulation output program has input summary sheets that closely mirror the data requested on one of these sheets (i.e. the lighting sheet), can that data be uploaded in lieu of the data on this sheet? Answer: Yes, however, the project team should ensure that the information provided from the energy simulation program is substantially similar to that requested on this spreadsheet. For example, a single average lighting power density number for the baseline and proposed case would not be acceptable. Instead, specific information should be provided regarding the building types or space types modeled, the baseline lighting power density associated with each building or space type, any lighting credit adjustments taken, and the overall weighted average lighting power densities for the Baseline and Proposed Case.
Question: Our project uses California Title-24, but the spreadsheet inputs are mostly specific to ASHRAE 90.1. How should we input the required information. Answer: This spreadsheet is focused on ASHRAE 90.1-2007 Appendix G. If using Title-24 to document compliance, please override the relevant baseline case inputs as necessary to indicate the Title-24 baseline information for the project.
Question: We have some suggestions for improving the form. Where can we make these suggestions? Answer: Please post all feedback to http://www.usgbc.org/ContactUS/LEEDContact.aspx. We appreciate your suggestions!

## Opaque Envelope
Table 1.4.1 - Opaque Building Envelope
Instructions: Complete the Opaque Building Envelope Requirements section, then describe each unique opaque building envelope construction on a separate row in the Opaque Building Envelope Constructions table (required inputs are green). Note that extra rows can be added using the button to the lower left of each construction type as necessary. An example of the expected level of detail has been provided for each type of construction. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". Baseline Case Information will autogenerate for New Construction Opaque Assemblies when the space conditioning category is selected. | [8 empty] | 1 2 3 4 5 6
Opaque Building Envelope Requirements
For projects modeled using ASHRAE 90.1-2007 Appendix G, select the climate zone: | [9 empty] | 0
[10 empty] | 100% NC | 100% EB | NC/EB
Select the appropriate description for the project: | [8 empty] | 1 2 3 4 5 | 1 | 0 | 0 |  | 1
| For existing spaces, have there been any changes to the space conditioning category (for example, previously unconditioned spaces becoming fully conditioned)? | [7 empty] | 1 2 3 4 5 6 | 0 | 0 |  |  | 0
Check the applicable space conditioning categories included in the project: | [8 empty] | 1 2 | FALSE | FALSE | FALSE | FALSE
| All spaces qualifying as semiheated are not defined as heated per Table 3.1 or indirectly conditioned (see Section 3.2 definition of space) | [7 empty] | 1 2 | 0 | 0 |  |  | 0
| Opaque envelope assemblies separating conditioned space from unconditioned or semiheated space are modeled using semiheated envelope assemblies per the ASHRAE 90.1-2007 User's Manual, Section 5.1.1, Envelope Component Assemblies (Page 5-2). | [8 empty] | 0 | 0 |  |  | 0
All Baseline new construction opaque envelope assemblies were modeled as required by Table 5.5 for the project's climate zone and Table G3.1#5(b) as delayed assemblies. See the Helpful Notes for each opaque assembly for more information. | [8 empty] | 1 2
All Baseline existing roofs, above-grade exterior walls, below-grade exterior walls, exposed floors, slab-on-grade floors, and opaque doors were modeled using the existing conditions prior to any revisions in spaces with unchanged space conditioning categories | [8 empty] | 1 2
All Proposed roofs, above-grade exterior walls, below-grade exterior walls, exposed floors, slab-on-grade floors, and opaque doors were modeled as-designed and with assembly U-factors / C-factors / F-factors consistent with Appendix A values | [8 empty] | 1 2
Infiltration rates and schedules have been modeled identically in the Baseline and Proposed case | [8 empty] | 1
For each item entered as “No” above, describe the applicable ASHRAE 90.1 Appendix G exception(s) that apply, or the circumstances preventing the opaque envelope parameters from being modeled as required. If the energy simulation software is not capable of modeling the required parameters, describe the adjustments that were made to provide a thermodynamically similar representation or provide a narrative justifying why the predicted energy performance results will not be influenced: | [8 empty] | 1 2 3 4
1 2 3
Opaque Building Envelope Constructions
Model Input Parameter | New / Existing | Space-Conditioning Category | Baseline Case |  | Proposed Case |  | Baseline Roof Reflectivity Modeled as 0.3? | Proposed Roof Reflectivity Modeled
|  |  | Description | Assembly U-factor/ C-factor/ F-factor | Description | Assembly U-factor/ C-factor/ F-factor
Roof Constructions | Helpful Notes: |  | •New roofs: insulation entirely above deck with U-factor from appropriate Table 5.5 per Table G3.1#5(b). •Existing roofs: existing conditions per Table G3.1#5(f). |  | Proposed construction assembly U-factor should be as-designed and consistent with Appendix A of ASHRAE 90.1 (list Appendix A Table referenced) |  | 0.3 per Table G3.1#5(e) | 0.3 or 0.45 per Table G3.1#5(c) | 1 2 3 4 | 0 | 0
[9 empty] | 1 2 | 0 | 0
[9 empty] | 1 2 | 0 | 0
Above-Grade Exterior Wall Constructions | Helpful Notes: |  | •New above-grade walls: steel-framed with U-factor from appropriate Table 5.5 per Table G3.1#5(b). •Existing above-grade walls: existing conditions per Table G3.1#5(f). |  | Proposed construction assembly U-factor should be as-designed and consistent with Appendix A of ASHRAE 90.1 (list Appendix A Table referenced) |  |  |  | 1 2 3 4 5 | 0 | 0
[9 empty] | 1 2 | 0 | 0
[9 empty] | 1 2 | 0 | 0
Below-Grade Exterior Wall Constructions | Helpful Notes: |  | •New below-grade walls: 8" medium weight concrete block with solid grouted cores as defined in A4.1 with C-factor from appropriate Table 5.5 per Table G3.1#5(b). •Existing below-grade walls: existing conditions per Table G3.1#5(f). |  | Proposed construction assembly C-factor should be as-designed and consistent with Appendix A of ASHRAE 90.1 (list Appendix A Table referenced) |  |  |  | 1 2 3 4 5 6 | 0 | 0
[9 empty] | 1 2 | 0 | 0
[9 empty] | 1 2 | 0 | 0
Exposed Floor Constructions | Helpful Notes: |  | •New floors: steel-joist with U-factor from appropriate Table 5.5 per Table G3.1#5(b). •Existing floors: existing conditions per Table G3.1#5(f). •For floor assemblies above unconditioned or semiheated space, select the space conditioning category as semiheated per 90.1-2007 User's Manual, Section 5.1.1-Envelope Component Types (Figure 5-C) |  | Proposed construction assembly U-factor should be as-designed and consistent with Appendix A of ASHRAE 90.1 (list Appendix A Table referenced) |  |  |  | 1 2 3 4 5 6 7 8 | 0 | 0
[9 empty] | 1 2 | 0 | 0
[9 empty] | 1 2 | 0 | 0
Slab-On-Grade Floors | Helpful Notes: |  | •New slab-on-grade floors: unheated 6" concrete slab with F-factor from appropriate Table 5.5 per Table G3.1#5(b). •Existing slab-on-grade floors: existing conditions per Table G3.1#5(f). |  | Proposed construction assembly F-factor should be as-designed and consistent with Appendix A of ASHRAE 90.1 (list Appendix A Table referenced) |  |  |  | 1 2 3 4 5 | 0 | 0
[9 empty] | 1 2 | 0 | 0
[9 empty] | 1 2 | 0 | 0
Opaque Doors | Helpful Notes: |  | •New opaque doors: U-factor from appropriate Table 5.5 per Table G3.1#5(b). •Existing opaque doors: existing conditions per Table G3.1#5(f). |  | Proposed construction assembly U-factor should be as-designed and consistent with A7.1 of ASHRAE 90.1 for unlabeled doors |  |  |  | 1 2 3 4 5 | 0 | 0
[9 empty] | 1 2 | 0 | 0
[9 empty] | 1 2 | 0 | 0
Additional notes:
The project is 100% new construction
The project is 100% existing renovation
The project is a combination of new construction and existing renovation
No changes to space conditioning categories
Yes, and the associated constructions in the Baseline case have been modeled using the Appendix G requirements for new constructions
Nonresidential
Residential
Semiheated
Unconditioned
Yes
N/A (no semiheated spaces)
Yes
N/A (no opaque assemblies separating conditioned and semiheated / unconditioned space)
Add a Roof Assembly
Add a Wall Assembly
Add a Wall Assembly
Add a Floor Assembly
Add a Floor Assembly
Add a Door Type

## QC Checklist (hidden)
|  |  |  | 1 | 1
Quality Control Checklist |  |  |  | 1 | 1
Instructions: Verify and then check off each of the items in the list below |  |  |  | 1 | 1
| Nonresidential | Residential | Semiheated | 1 | 1
Check the applicable space conditioning categories included in the project: | TRUE | FALSE |  | 1 | 1
Check this box if the project is new construction or includes a new addition: | TRUE |  |  | 1 | 1
Check this box if the project includes any existing renovation: | TRUE |  |  | 1 | 1
Select the project's Climate Zone (see Appendix B of ASHRAE 90.1-2007): | 4A |  |  | 1 | 1
|  |  |  | 1 | 1
Opaque Building Envelope | Yes | No | N/A | 1 | 1
9 |  |  |  | 1 | 1
R-20 insulation entirely above deck with a U-factor of 0.048 |  |  |  | 0 | 1
R-20 insulation entirely above deck with a U-factor of 0.048 |  |  |  | 0 | 1
R-5.0 insulation entirely above deck with a U-factor of 0.173 |  |  |  | 1 | 1
steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 |  |  |  | 0 | 1
steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 |  |  |  | 0 | 1
steel-framed with R-13 cavity insulation with a U-factor of 0.124 |  |  |  | 1 | 1
8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 |  |  |  | 0 | 1
8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 |  |  |  | 0 | 1
8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 |  |  |  | 1 | 1
steel-joist with R-30 insulation with a U-factor of 0.038 |  |  |  | 0 | 1
steel-joist with R-30 insulation with a U-factor of 0.038 |  |  |  | 0 | 1
steel-joist with R-13 insulation with a U-factor of 0.069 |  |  |  | 1 | 1
6" concrete slabs with no insulation with an F-factor of 0.730 |  |  |  | 0 | 1
6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 |  |  |  | 0 | 1
6" concrete slabs with no insulation with an F-factor of 0.730 |  |  |  | 1 | 1
U-factor of 0.700 |  |  |  | 0 | 1
U-factor of 0.700 |  |  |  | 0 | 1
U-factor of 0.700 |  |  |  | 1 | 1
U-factor of 1.500 |  |  |  | 0 | 1
U-factor of 0.500 |  |  |  | 0 | 1
Existing Renovations: All existing Baseline roofs, above-grade exterior walls, below-grade exterior walls, exposed floors, slab-on-grade floors, and opaque doors were modeled using the existing conditions prior to any revisions |  |  |  | 1 | 1
New
Existing

## Envelope Lookup
Climate Zone | Hlookup Number | Nonresidential Roof | Residential Roof | Semiheated Roof | Nonresidential Above-Grade Exterior Wall | Residential Above-Grade Exterior Wall | Semiheated Above-Grade Exterior Wall | Nonresidential Below-Grade Exterior Wall | Residential Below-Grade Exterior Wall | Semiheated Below-Grade Exterior Wall | Nonresidential Exposed Floor | Residential Exposed Floor | Semiheated Exposed Floor | Nonresidential Slab-On-Grade Floor | Residential Slab-On-Grade Floor | Semiheated Slab-On-Grade Floor | Nonresidential Opaque Swinging Doors | Residential Opaque Swinging Doors | Semiheated Opaque Swinging Doors | Nonresidential Opaque Nonswinging Doors | Residential Opaque Nonswinging Doors | Semiheated Opaque Nonswinging Doors | Nonmetal framing (all) | Metal framing (curtainwall/storefront) | Metal framing (entrance door) | Metal framing (all other) | SHGC | Skylight with Curb, Glass, 0%-2.0% | Skylight with Curb, Glass, 2.1%-5.0% | Skylight with Curb, Plastic, 0%-2.0% | Skylight with Curb, Plastic, 2.1%-5.0% | Skylight without Curb, All, 0%-2.0% | Skylight without Curb, All, 2.1%-5.0% | Skylight with Curb, Glass, 0%-2.0% | Skylight with Curb, Glass, 2.1%-5.0% | Skylight with Curb, Plastic, 0%-2.0% | Skylight with Curb, Plastic, 2.1%-5.0% | Skylight without Curb, All, 0%-2.0% | Skylight without Curb, All, 2.1%-5.0% | Nonresidential Roof | Residential Roof | Semiheated Roof | Nonresidential Above-Grade Exterior Wall | Residential Above-Grade Exterior Wall | Semiheated Above-Grade Exterior Wall | Nonresidential Below-Grade Exterior Wall | Residential Below-Grade Exterior Wall | Semiheated Below-Grade Exterior Wall | Nonresidential Exposed Floor | Residential Exposed Floor | Semiheated Exposed Floor | Nonresidential Slab-On-Grade Floor | Residential Slab-On-Grade Floor | Semiheated Slab-On-Grade Floor | Nonresidential Opaque Swinging Doors | Residential Opaque Swinging Doors | Semiheated Opaque Swinging Doors | Nonresidential Opaque Nonswinging Doors | Residential Opaque Nonswinging Doors | Semiheated Opaque Nonswinging Doors | New/Existing | Space Conditioning Category
1A | 2 | R-15 insulation entirely above deck with a U-factor of 0.063 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-3.8 insulation entirely above deck with a U-factor of 0.218 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | steel-framed with no insulation with a U-factor of 0.352 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with no insulation with a U-factor of 0.350 | steel-joist with no insulation with a U-factor of 0.350 | steel-joist with no insulation with a U-factor of 0.350 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.450 | U-factor of 1.450 | U-factor of 1.450 | 1.2 | 1.2 | 1.2 | 1.2 | 0.25 | 1.98 | 1.98 | 1.9 | 1.9 | 1.36 | 1.36 | 0.36 | 0.19 | 0.34 | 0.27 | 0.36 | 0.19 | U-0.063 | U-0.048 | U-0.218 | U-0.124 | U-0.124 | U-0.352 | C-1.140 | C-1.140 | C-1.140 | U-0.350 | U-0.350 | U-0.350 | F-0.730 | F-0.730 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.450 | U-1.450 | U-1.450 | New | Nonresidential
1B | 3 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-3.8 insulation entirely above deck with a U-factor of 0.218 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | steel-framed with no insulation with a U-factor of 0.352 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with no insulation with a U-factor of 0.350 | steel-joist with no insulation with a U-factor of 0.350 | steel-joist with no insulation with a U-factor of 0.350 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.450 | U-factor of 1.450 | U-factor of 1.450 | 1.2 | 1.2 | 1.2 | 1.2 | 0.25 | 1.98 | 1.98 | 1.9 | 1.9 | 1.36 | 1.36 | 0.36 | 0.19 | 0.34 | 0.27 | 0.36 | 0.19 | U-0.063 | U-0.048 | U-0.218 | U-0.124 | U-0.124 | U-0.352 | C-1.140 | C-1.140 | C-1.140 | U-0.350 | U-0.350 | U-0.350 | F-0.730 | F-0.730 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.450 | U-1.450 | U-1.450
2A | 4 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-3.8 insulation entirely above deck with a U-factor of 0.218 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.450 | U-factor of 0.500 | U-factor of 1.450 | 0.75 | 0.7 | 1.1 | 0.75 | 0.25 | 1.98 | 1.98 | 1.9 | 1.9 | 1.36 | 1.36 | 0.36 | 0.19 | 0.39 | 0.34 | 0.36 | 0.19 | U-0.048 | U-0.048 | U-0.218 | U-0.124 | U-0.064 | U-0.124 | C-1.140 | C-1.140 | C-1.140 | U-0.052 | U-0.052 | U-0.069 | F-0.730 | F-0.730 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.450 | U-0.500 | U-1.450
2B | 5 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-3.8 insulation entirely above deck with a U-factor of 0.218 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.450 | U-factor of 0.500 | U-factor of 1.450 | 0.75 | 0.7 | 1.1 | 0.75 | 0.25 | 1.98 | 1.98 | 1.9 | 1.9 | 1.36 | 1.36 | 0.36 | 0.19 | 0.39 | 0.34 | 0.36 | 0.19 | U-0.048 | U-0.048 | U-0.218 | U-0.124 | U-0.064 | U-0.124 | C-1.140 | C-1.140 | C-1.140 | U-0.052 | U-0.052 | U-0.069 | F-0.730 | F-0.730 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.450 | U-0.500 | U-1.450
3A | 6 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-5.0 insulation entirely above deck with a U-factor of 0.173 | steel-framed with R-13 cavity and R-3.8 continuous insulation with a U-factor of 0.084 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.450 | U-factor of 0.500 | U-factor of 1.450 | 0.65 | 0.6 | 0.9 | 0.65 | 0.25 | 1.17 | 1.17 | 1.3 | 1.3 | 0.69 | 0.69 | 0.39 | 0.19 | 0.65 | 0.34 | 0.39 | 0.19 | U-0.048 | U-0.048 | U-0.173 | U-0.084 | U-0.064 | U-0.124 | C-1.140 | C-1.140 | C-1.140 | U-0.052 | U-0.052 | U-0.069 | F-0.730 | F-0.730 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.450 | U-0.500 | U-1.450
3B | 7 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-5.0 insulation entirely above deck with a U-factor of 0.173 | steel-framed with R-13 cavity and R-3.8 continuous insulation with a U-factor of 0.084 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.450 | U-factor of 0.500 | U-factor of 1.450 | 0.65 | 0.6 | 0.9 | 0.65 | 0.25 | 1.17 | 1.17 | 1.3 | 1.3 | 0.69 | 0.69 | 0.39 | 0.19 | 0.65 | 0.34 | 0.39 | 0.19 | U-0.048 | U-0.048 | U-0.173 | U-0.084 | U-0.064 | U-0.124 | C-1.140 | C-1.140 | C-1.140 | U-0.052 | U-0.052 | U-0.069 | F-0.730 | F-0.730 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.450 | U-0.500 | U-1.450
3C | 8 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-5.0 insulation entirely above deck with a U-factor of 0.173 | steel-framed with R-13 cavity and R-3.8 continuous insulation with a U-factor of 0.084 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-19 insulation with a U-factor of 0.052 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.450 | U-factor of 0.500 | U-factor of 1.450 | 0.65 | 0.6 | 0.9 | 0.65 | 0.25 | 1.17 | 1.17 | 1.3 | 1.3 | 0.69 | 0.69 | 0.39 | 0.19 | 0.65 | 0.34 | 0.39 | 0.19 | U-0.048 | U-0.048 | U-0.173 | U-0.084 | U-0.064 | U-0.124 | C-1.140 | C-1.140 | C-1.140 | U-0.052 | U-0.052 | U-0.069 | F-0.730 | F-0.730 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.450 | U-0.500 | U-1.450
4A | 9 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-5.0 insulation entirely above deck with a U-factor of 0.173 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.500 | U-factor of 0.500 | U-factor of 1.450 | 0.4 | 0.5 | 0.85 | 0.55 | 0.4 | 1.17 | 1.17 | 1.3 | 1.3 | 0.69 | 0.69 | 0.49 | 0.39 | 0.65 | 0.34 | 0.49 | 0.39 | U-0.048 | U-0.048 | U-0.173 | U-0.064 | U-0.064 | U-0.124 | C-1.140 | C-0.119 | C-1.140 | U-0.038 | U-0.038 | U-0.069 | F-0.730 | F-0.540 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.500 | U-0.500 | U-1.450
4B | 10 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-5.0 insulation entirely above deck with a U-factor of 0.173 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.500 | U-factor of 0.500 | U-factor of 1.450 | 0.4 | 0.5 | 0.85 | 0.55 | 0.4 | 1.17 | 1.17 | 1.3 | 1.3 | 0.69 | 0.69 | 0.49 | 0.39 | 0.65 | 0.34 | 0.49 | 0.39 | U-0.048 | U-0.048 | U-0.173 | U-0.064 | U-0.064 | U-0.124 | C-1.140 | C-0.119 | C-1.140 | U-0.038 | U-0.038 | U-0.069 | F-0.730 | F-0.540 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.500 | U-0.500 | U-1.450
4C | 11 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-5.0 insulation entirely above deck with a U-factor of 0.173 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-13 insulation with a U-factor of 0.069 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 0.700 | U-factor of 1.500 | U-factor of 0.500 | U-factor of 1.450 | 0.4 | 0.5 | 0.85 | 0.55 | 0.4 | 1.17 | 1.17 | 1.3 | 1.3 | 0.69 | 0.69 | 0.49 | 0.39 | 0.65 | 0.34 | 0.49 | 0.39 | U-0.048 | U-0.048 | U-0.173 | U-0.064 | U-0.064 | U-0.124 | C-1.140 | C-0.119 | C-1.140 | U-0.038 | U-0.038 | U-0.069 | F-0.730 | F-0.540 | F-0.730 | U-0.700 | U-0.700 | U-0.700 | U-1.500 | U-0.500 | U-1.450
5A | 12 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-7.6 insulation entirely above deck with a U-factor of 0.119 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 1.450 | 0.35 | 0.45 | 0.8 | 0.55 | 0.4 | 1.17 | 1.17 | 1.1 | 1.1 | 0.69 | 0.69 | 0.49 | 0.39 | 0.77 | 0.62 | 0.49 | 0.39 | U-0.048 | U-0.048 | U-0.119 | U-0.064 | U-0.064 | U-0.124 | C-0.119 | C-0.119 | C-1.140 | U-0.038 | U-0.038 | U- 0.052 | F-0.730 | F-0.540 | F-0.730 | U-0.700 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-1.450
5B | 13 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-7.6 insulation entirely above deck with a U-factor of 0.119 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 1.450 | 0.35 | 0.45 | 0.8 | 0.55 | 0.4 | 1.17 | 1.17 | 1.1 | 1.1 | 0.69 | 0.69 | 0.49 | 0.39 | 0.77 | 0.62 | 0.49 | 0.39 | U-0.048 | U-0.048 | U-0.119 | U-0.064 | U-0.064 | U-0.124 | C-0.119 | C-0.119 | C-1.140 | U-0.038 | U-0.038 | U- 0.052 | F-0.730 | F-0.540 | F-0.730 | U-0.700 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-1.450
5C | 14 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-7.6 insulation entirely above deck with a U-factor of 0.119 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with no insulation with an F-factor of 0.730 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 1.450 | 0.35 | 0.45 | 0.8 | 0.55 | 0.4 | 1.17 | 1.17 | 1.1 | 1.1 | 0.69 | 0.69 | 0.49 | 0.39 | 0.77 | 0.62 | 0.49 | 0.39 | U-0.048 | U-0.048 | U-0.119 | U-0.064 | U-0.064 | U-0.124 | C-0.119 | C-0.119 | C-1.140 | U-0.038 | U-0.038 | U- 0.052 | F-0.730 | F-0.540 | F-0.730 | U-0.700 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-1.450
6A | 15 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-10.0 insulation entirely above deck with a U-factor of 0.093 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-38 insulation with a U-factor of 0.032 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with R-15 insulation for 24 in. with an F-factor of 0.520 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 1.450 | 0.35 | 0.45 | 0.8 | 0.55 | 0.4 | 1.17 | 1.17 | 0.87 | 0.87 | 0.69 | 0.69 | 0.49 | 0.49 | 0.71 | 0.58 | 0.49 | 0.49 | U-0.048 | U-0.048 | U-0.093 | U-0.064 | U-0.064 | U-0.124 | C-0.119 | C-0.119 | C-1.140 | U-0.038 | U-0.032 | U- 0.052 | F-0.540 | F-0.520 | F-0.730 | U-0.700 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-1.450
6B | 16 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-10.0 insulation entirely above deck with a U-factor of 0.093 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-38 insulation with a U-factor of 0.032 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with R-10 insulation for 24 in. with an F-factor of 0.540 | 6" concrete slabs with R-15 insulation for 24 in. with an F-factor of 0.520 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 1.450 | 0.35 | 0.45 | 0.8 | 0.55 | 0.4 | 1.17 | 1.17 | 0.87 | 0.87 | 0.69 | 0.69 | 0.49 | 0.49 | 0.71 | 0.58 | 0.49 | 0.49 | U-0.048 | U-0.048 | U-0.093 | U-0.064 | U-0.064 | U-0.124 | C-0.119 | C-0.119 | C-1.140 | U-0.038 | U-0.032 | U- 0.052 | F-0.540 | F-0.520 | F-0.730 | U-0.700 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-1.450
7A | 17 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-10.0 insulation entirely above deck with a U-factor of 0.093 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-15.6 continuous insulation with a U-factor of 0.042 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-10.0 insulation with a C-factor of 0.092 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-38 insulation with a U-factor of 0.032 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with R-15 insulation for 24 in. with an F-factor of 0.520 | 6" concrete slabs with R-15 insulation for 24 in. with an F-factor of 0.520 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 1.450 | 0.35 | 0.4 | 0.8 | 0.45 | 0.45 | 1.17 | 1.17 | 0.87 | 0.87 | 0.69 | 0.69 | 0.68 | 0.64 | 0.77 | 0.71 | 0.68 | 0.64 | U-0.048 | U-0.048 | U-0.093 | U-0.064 | U-0.042 | U-0.124 | C-0.119 | C-0.092 | C-1.140 | U-0.038 | U-0.032 | U- 0.052 | F-0.520 | F-0.520 | F-0.730 | U-0.500 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-1.450
7B | 18 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-10.0 insulation entirely above deck with a U-factor of 0.093 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-15.6 continuous insulation with a U-factor of 0.042 | steel-framed with R-13 cavity insulation with a U-factor of 0.124 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-10.0 insulation with a C-factor of 0.092 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-30 insulation with a U-factor of 0.038 | steel-joist with R-38 insulation with a U-factor of 0.032 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with R-15 insulation for 24 in. with an F-factor of 0.520 | 6" concrete slabs with R-15 insulation for 24 in. with an F-factor of 0.520 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 1.450 | 0.35 | 0.4 | 0.8 | 0.45 | 0.45 | 1.17 | 1.17 | 0.87 | 0.87 | 0.69 | 0.69 | 0.68 | 0.64 | 0.77 | 0.71 | 0.68 | 0.64 | U-0.048 | U-0.048 | U-0.093 | U-0.064 | U-0.042 | U-0.124 | C-0.119 | C-0.092 | C-1.140 | U-0.038 | U-0.032 | U- 0.052 | F-0.520 | F-0.520 | F-0.730 | U-0.500 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-1.450
8 | 19 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-20 insulation entirely above deck with a U-factor of 0.048 | R-15.0 insulation entirely above deck with a U-factor of 0.063 | steel-framed with R-13 cavity and R-7.5 continuous insulation with a U-factor of 0.064 | steel-framed with R-13 cavity and R-18.8 continuous insulation with a U-factor of 0.037 | steel-framed with R-13 cavity and R-3.8 continuous insulation with a U-factor of 0.084 | 8" medium weight concrete block with solid grouted cores and R-7.5 insulation with a C-factor of 0.119 | 8" medium weight concrete block with solid grouted cores and R-12.5 insulation with a C-factor of 0.075 | 8" medium weight concrete block with solid grouted cores and no insulation with a C-factor of 1.140 | steel-joist with R-38 insulation with a U-factor of 0.032 | steel-joist with R-38 insulation with a U-factor of 0.032 | steel-joist with R-19 insulation with a U-factor of 0.052 | 6" concrete slabs with R-15 insulation for 24 in. with an F-factor of 0.520 | 6" concrete slabs with R-20 insulation for 24 in. with an F-factor of 0.510 | 6" concrete slabs with no insulation with an F-factor of 0.730 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 0.700 | U-factor of 0.500 | U-factor of 0.500 | U-factor of 0.500 | 0.35 | 0.4 | 0.8 | 0.45 | 0.45 | 0.98 | 0.98 | 0.61 | 0.61 | 0.58 | 0.58 | 0.68 | 0.64 | 0.77 | 0.71 | 0.68 | 0.64 | U-0.048 | U-0.048 | U-0.063 | U-0.064 | U-0.037 | U-0.084 | C-0.119 | C-0.075 | C-1.140 | U-0.032 | U-0.032 | U- 0.052 | F-0.520 | F-0.510 | F-0.730 | U-0.500 | U-0.500 | U-0.700 | U-0.500 | U-0.500 | U-0.500

## Shading & Fenestration
Table 1.4.2A - Shading & Orientation
Instructions: Provide the following shading and orientation information (required inputs are green). An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". | [9 empty] | 1 2 3 4 |  | 0
Model Input Parameter |  |  | Baseline Case |  |  | Proposed Case
Helpful Notes: |  |  | •All vertical glazing flush with exterior wall and no shading projections per Table G3.1#5(c) •No manual shading devices such as blinds or shades per Table G3.1#5(c) •No self-shading per Table G3.1#5 •Total vertical fenestration areas for new construction equal to Proposed up to 40% maximum, and distributed on each face of the building in the same proportions as the Proposed design per Table G3.1#5(c) •Total skylight area for new construction equal to Proposed up to 5% maximum per Table G3.1#5(d) |  |  | •No manual shading devices such as blinds or shades per Table G3.1#5(d) •Permanent shading devices (such as fins, overhangs, and light shelves) and automatically controlled shades or blinds may be modeled per Table G3.1#5(d) •Shading by adjacent structures and terrain may be modeled, but must be modeled identically in the Baseline case |  |  |  | 1 2 3 4 5 6 7 8 9 10 11 12
Shading Devices |  |  | No shading projections, manual shading devices, or self-shading have been modeled for the Baseline building Any shading by adjacent structures and terrain has been modeled identically to the Proposed case (if applicable) | [6 empty] | 1 2 3 4 5 6
Building Shape & Orientation |  |  | The Baseline building is modeled with the same shape and orientation as the Proposed building, and for new construction rotated 90°, 180°, and 270° | [6 empty] | 1 2 3 4
Above-Grade Wall & Vertical Glazing Area by Orientation |  | Orientation | Above-Grade Wall Area (ft2) | Vertical Glazing Area |  | Above-Grade Wall Area (ft2) | Vertical Glazing Area |  |  | 1 2
|  |  |  | (ft2) | (%) |  | (ft2) |  | (%)
|  | North | Identical to Proposed case
|  | East | Identical to Proposed case
|  | South | Identical to Proposed case
|  | West | Identical to Proposed case
|  | Total | Identical to Proposed case | 0 |  | 0 | 0
Roof & Skylight Area |  |  | Roof Area (ft2) | Skylight Area |  | Roof Area (ft2) | Skylight Area
|  |  |  | (ft2) | (%) |  | (ft2) |  | (%)
Identical to Proposed case
Table 1.4.2B - Fenestration
Instructions: Describe each unique fenestration assembly on a separate row in the following table (required inputs are green). Note that additional rows can be expanded using the Add a Line button to the lower left of each fenestration type as necessary. An example of the expected level of detail has been provided for each type of fenestration. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". Baseline Case Information will autogenerate for New Construction Nonresidential or Residential Vertical Glazing and for New Construction Nonresidential skylights when the Baseline Description is selected from one of the items listed. | [9 empty] | 1 2 3 4 5
Model Input Parameter | New / Existing | Space-Conditioning Category | Baseline Case |  |  | Proposed Case
|  |  | Description | Assembly U-factor | SHGC | Description | Assembly U-factor | SHGC | VLT
Vertical Glazing | Helpful Notes: |  | •New vertical glazing: assembly U-factor and SHGC from appropriate Table 5.5 per Table G3.1#5(c). •Existing vertical glazing: existing conditions per Table G3.1#5(f). |  |  | Proposed vertical glazing assembly U-factor should be as-designed and account for the impact of the frames on the whole assembly. Reference Table A8.2 of ASHRAE 90.1 as necessary. |  |  |  | 1 2 3 4 | 0 | 0 | 0
| New |  | Nonmetal framing (all) | [6 empty] | 1 2 | 0 | 0 | 0
| New | [8 empty] | 1 2 | 0 | 0 | 0
Skylights | Helpful Notes: |  | •New skylights: assembly U-factor and SHGC from appropriate Table 5.5 per Table G3.1#5(d). •Existing skylights: existing conditions per Table G3.1#5(f). |  |  | Proposed skylight assembly U-factor should be as-designed and account for the impact of the frames on the whole assembly. Reference Tables A8.1A and A8.1B of ASHRAE 90.1 as necessary. |  |  |  | 1 2 3 4 | 0 | 0 | 0
| New | [8 empty] | 1 2 | 0 | 0 | 0
| New | [8 empty] | 1 2 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0
How were the Proposed case framed assembly fenestration U-factors determined?
Additional notes:
NFRC testing for site-assembled fenestration
NFRC testing for manufactured fenestration assemblies
Table A8.2 (windows) and Table A8.1 (skylights)
LBNL Window 5 or Window 6 calculations
Energy simulation includes separate frame and glazing
Other (Describe)
Add a Glazing Type
Add a Skylight Type

## Lighting
1
Table 1.4.3A - Interior Lighting | [9 empty] | 1
Instructions: Confirm that the energy model complies with the Interior lighting requirements listed, and provide a narrative explaining any discrepancies. Select the interior lighting categorization procedure, and then complete the corresponding lighting table (required inputs are green). An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". For projects using California Title-24, the following Title-24 lighting compliance forms may be uploaded in lieu of this sheet (2008 - LTG-1C, LTG-2C, LTG-3C, LTG-5-C, OLTG-1C, OLTG-2C, SLTG-1C; 2005 - LTG-1C, LTG-2-C, LTG-3-C, LTG-4-C, LTG-5-C, LTG-9-C, OLTG-1-C, OLTG-2-C, OLTG-3-C, OLTG-4-C). | [8 empty] | 1 2 3 4 | 1
Interior Lighting Requirements | [9 empty] | 1
All lighting schedules have been modeled identically in the Baseline and Proposed case and reflect the anticipated operating schedules of each space | [8 empty] | 1 2 | 1
The Proposed lighting power includes all lighting system components shown or provided for on the plans (including lamps and ballasts and task and furniture-mounted fixtures except where specifically exempted) | [8 empty] | 1 2 | 1
Per ASHRAE 90.1-2007, Section 9.1.4 (c), and (d): For all line-voltage lighting track and plug-in busway, designed to allow the addition and/or relocation of luminaires without altering the wiring of the system, the proposed case wattage is modeled as: (a) the specified wattage of the luminaires included in the system with a minimum of 30 W/lin ft, OR (b) the wattage limit of the system's circuit breaker, OR (c) the wattage limit of other permanent current-limiting device(s) For all low-voltage lighting track, cable conductor, rail conductor, and other flexible lighting systems that allow the addition and/or relocation of luminaires without altering the wiring of the system, the proposed case wattage is modeled as the wattage of the transformer supplying the system.
For each item entered as “No” above, describe the applicable ASHRAE 90.1 Appendix G exception(s) that apply, or the circumstances preventing the lighting parameters from being modeled as required. If the energy simulation software is not capable of modeling the required parameters, describe the adjustments that were made to provide a similar representation or provide a narrative justifying why the predicted energy performance results will not be influenced: | [8 empty] | 1 2 3 4
1 2 3
1
Categorization Procedure | [9 empty] | 1
Select the categorization procedure (Building Area or Space by Space Method) used to determine the lighting power density (LPD) in the Proposed and Baseline case | [8 empty] | 1 2 3 | 1 | 0 | 0 | 0
1
Building Area Method | [9 empty] | 0
Table 9.5.1 Building Area Type | Total Area of Building Type (ft2) | Baseline Case |  | Proposed Case | [5 empty] | 0
|  | Modeled LPD (W/ft2) |  | Design LPD (W/ft2) | Automatic Lighting Controls and Space Types | Table G3.2 Power Adjust-ment | Modeled LPD (W/ft2) | Daylighting Controls |  | 0
Helpful Notes: Parking garages are always considered a separate building area type, and if present in the building, must be listed as a separate building area type from the main building area type |  | Modeled using the maximum allowance from Table 9.5.1 (values provided for reference - overwrite if modeled differently) |  | •Lighting power should be modeled as designed (or installed) including all lighting system components (lamps and ballasts) •Credit for automatic lighting controls should be modeled using the appropriate power adjustment from Table G3.2, applied only to the controlled lighting power and not where required by 9.4.1.2 per Table G3.1#6(g) [conference rooms; meeting rooms; employee lunch and break rooms; classrooms excepting Pre-K through 12th grade, laboratory, or shop] •Automatic daylighting controls must either be modeled directly in the simulation, or modeled using schedule adjustments determined by a separate daylighting analysis per Table G3.1#6(f) |  |  |  |  | 1 2 3 4 5 6 7 8 | 0
[10 empty] | 0 | 1
[10 empty] | 0 | 1
Total | 0 | [8 empty] | 0
[9 empty] | 1 2 | 0
Space by Space Method | [9 empty] | 0
Table 9.6.1 Space Type | Total Area of Space Type (ft2) | Baseline Case |  | Proposed Case | [5 empty] | 0
|  | Modeled LPD (Excluding Section 9.6.2 Additional Lighting) (W/ft2) |  | Design LPD (Excluding Section 9.6.2 Additional Lighting) (W/ft2) | Automatic Lighting Controls and Space Types | Table G3.2 Power Adjust-ment | Modeled LPD (W/ft2) | Daylighting Controls | 1 2 3 4 5 | 0
Helpful Notes: Refer to 90.1 User's Manual for definitions of Active vs. Inactive Storage, General Low Bay vs. General High Bay Manufacturing, and Fine vs. Medium/Bulky Material Storage Warehouse |  | Modeled using the maximum allowance from Table 9.6.1 (values provided for reference - overwrite if modeled differently) |  | •Lighting power should be modeled as designed (or installed) including all lighting system components (lamps and ballasts) •Credit for automatic lighting controls should be modeled using the appropriate power adjustment from Table G3.2, applied only to the controlled lighting power and not where required by 9.4.1.2 per Table G3.1#6(g) [conference rooms; meeting rooms; employee lunch and break rooms; classrooms excepting Pre-K through 12th grade, laboratory, or shop] •Automatic daylighting controls must either be modeled directly in the simulation, or modeled using schedule adjustments determined by a separate daylighting analysis per Table G3.1#6(f) |  |  |  |  | 1 2 3 4 5 6 7 8 | 0
[10 empty] | 0 | 1
[10 empty] | 0 | 1
[10 empty] | 0 | 1
[10 empty] | 0 | 1
[10 empty] | 0 | 1
Total | 0 | [8 empty] | 0
[9 empty] | 1 2 | 0
Section 9.6.2 Additional Lighting Power (if applicable) | [6 empty] | Verify that the additional lighting power has been modeled as required by selecting "Yes". |  | 1 2 3 | 0
Table 9.6.1 Space Type | Total Area of Space Type (ft2) | Additional Lighting Power Description |  |  | Additional LPD (W/ft2) |  |  | The additional lighting schedule has been modeled separately from the general lighting schedule to reflect the differing controls | 1 2 3 | 0 | FALSE
Helpful Notes: |  | •May be modeled only when installed and automatically controlled, separately from the general lighting, to be turned off during non-business hours •Schedule must be modeled separately from the general lighting schedule •Lighting power must be modeled identically in the Baseline and Proposed case up to the value allowed in 9.6.2 | [5 empty] | Additional lighting power has been modeled identically in the Baseline and Proposed case up to the value allowed in Section 9.6.2 | 1 2 3 4 5 6 7 | 0 | FALSE
0
0
Total | 0 | [8 empty] | 0
[9 empty] | 1 2 | 0
Interior Process Lighting (if applicable) | [9 empty] | 1
Description |  |  | Section 9.2.2.3 Exemption |  | Total Process Lighting Power (Watts) | Modeled Identically In Baseline? |  |  |  | 1
Helpful Notes: |  |  | Any lighting not regulated by ASHRAE 90.1 is considered process and must be modeled identically in the Proposed and Baseline case unless an Exceptional Calculation is submitted | [5 empty] | 1 2 3 | 1
[9 empty] | 1 2 3 | 1 | 0 |  | 1
1
1
Table 1.4.3B - Exterior Lighting | [9 empty] | 1
Instructions: Select the applicable exterior lighting categories and then complete the corresponding lighting table(s) (required inputs are green). An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". | [8 empty] | 1 2 3 4 | 1
Exterior Lighting Requirements | [9 empty] | 1
The exterior lighting power values reported below are consistent with the SSc8 (Light Pollution Reduction Form) | [8 empty] | 1 2 3 | 1
Additional lighting power allowance has not been claimed in the Baseline case for surfaces that are not provided with lighting in the actual design and lighting fixtures have not been double-counted for different exterior surfaces | [8 empty] | 1 2 | 1
1
Exterior Lighting Categories | [9 empty] | 1 | FALSE
Check all applicable exterior lighting categories (Tradable and/or Nontradable) included in the project (program takes a few seconds to generate input table) | [8 empty] | 1 2 3 | 1 | FALSE
1
Tradable Surfaces | [9 empty] | 0
Table 9.4.5 Tradable Exterior Lighting Application | Required Input (Area or Length) | Total Area (ft2) or Length (ft) | Baseline Case |  | Proposed Case |  |  |  |  | 0
|  |  | Allowed LPD | Lighting Power Allowance (Watts) | Design Lighting Power (Watts) |  |  |  |  | 0
Helpful Notes: •Only enter area or length of illuminated surface in the design •Fixtures cannot be double-counted for multiple exterior surface types |  |  | Allowance calculated using the maximum lighting power density from Table 9.4.5 |  | Lighting power should be modeled as designed (or installed) |  |  |  | 1 2 3 4 5 | 0
0
0
0
Subtotal: Tradable surface lighting allowance |  |  |  | 0 | 0 |  |  |  |  | 0
Total Tradable surface lighting allowance including 5% unrestricted allowance |  |  |  | 0 |  |  |  |  | 1 2 | 0
[9 empty] | 1 2 | 0
Nontradable Surfaces | [9 empty] | 0
Table 9.4.5 Nontradable Exterior Lighting Application | Required Input | Quantity of Required Input for Project | Baseline Case |  | Proposed Case |  |  |  |  | 0
|  |  | Allowed LPD | Lighting Power Allowance (Watts) | Design Lighting Power (Watts) |  |  |  |  | 0
Helpful Notes: •Only enter area or length of illuminated surface in the design •Fixtures cannot be double-counted for multiple exterior surface types |  |  | Total allowance calculated using the lesser of the design lighting power, or the lighting power allowance used, since no credit is permitted for nontradable surfaces |  | Lighting power should be modeled as designed (or installed) |  |  |  | 1 2 3 4 5 6 | 0
Building facades | [9 empty] | 0
ATMs and night depositories | Number of ATMs |  | 270 W + 90 W per additional | [5 empty] | 1 2 3 | 0
Entrances and gatehouse inspection stations at guarded facilities | Uncovered Area |  | 1.25 | [6 empty] | 0
Loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | Uncovered Area |  | 0.5 | [6 empty] | 0
Drive-through windows at fast food restaurants | Drive-throughs |  | 400 | [6 empty] | 0
Parking near 24-hour retail entrances | Main Entries |  | 800 | [6 empty] | 0
Subtotal: Nontradable surface lighting allowance |  |  |  | 0 | 0 |  |  |  |  | 0
Total Nontradable surface lighting allowance including 5% unrestricted allowance |  |  |  | 0 |  |  |  |  | 1 2 | 0
1
Input Parameter |  |  | Baseline Case |  | Proposed Case |  |  |  |  | 1
Total Exterior Lighting Power Calculated Above (Watts) |  |  | 0 |  | 0 |  |  |  |  | 1
Total Exterior Lighting Power Modeled (Watts) | [9 empty] | 1
Additional notes: | [9 empty] | 1
1
1
Yes
No
The project includes Tradable Exterior Lighting
The project includes Nontradable Exterior Lighting
Building Area Method
Space by Space Method

## Equipment
1
Table 1.4.4 - Process Equipment | [5 empty] | 1
Instructions: Select the method used to model receptacle equipment, and then complete the corresponding receptacle equipment table (required inputs are green). Other process equipment should be reported in the bottom table. An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". |  |  |  |  | 1 2 3 4 | 1
Process Equipment Requirements | [5 empty] | 1
All receptacle equipment and other process equipment designed or anticipated for the building have been accounted for in the energy models. |  |  |  |  | 1 2 | 1
If process energy accounts for less than 25% of the total Baseline energy cost, an additional narrative justification for the low process cost has been provided in the supporting documentation. Note: process energy should not be arbitrarily set to 25% of the total Baseline cost, but should reflect the actual process loads anticipated for the building. |  |  |  |  | 1 2 3 | 1
1
If any of the process equipment requirements are indicated as "No" above, the project does not likely comply with LEED modeling requirements. It is recommended that the project team pursue a "Credit Interpretation Ruling" to justify the modeling approach. Please also provide any further information below to justify the modeling approach used. | [5 empty] | 1 |  |  | 1 2 3 4
[6 empty] | 1 |  |  | 1 2 3
1
Receptacle Equipment Modeling Method | [5 empty] | 1 | FALSE
Indicate whether the receptacle equipment was modeled using an average equipment power density for the building, equipment power densities by space type, or by entering the power associated with specific devices in each space (may select more than one) |  |  |  |  | 1 2 3 4 5 | 1 | FALSE
[6 empty] | 1 | FALSE
[6 empty] | 1 | FALSE
Building Average Equipment Power Density | [5 empty] | 0
Building Type | Total Area of Building Type | Equipment Power Density (W/ft2) | Equipment Included in Power Density | Baseline Modeled Identically? |  | 0
Helpful Notes: | •All receptacle loads must be modeled identically between the Proposed and Baseline case and included in the simulations per Table G3.1#12 •Any credit for improved receptacle equipment must be submitted using the Exceptional Calculation Method |  |  |  | 1 2 3 | 0
0
0
0
Total | 0 | 0 | Total Power Modeled Using Building Average Method (kW): | 0 | 1 2 | 0
[5 empty] | 1 2 | 0 |  | 0
Space by Space Equipment Power Densities | [5 empty] | 0
Space Type | Total Area of Space Type | Equipment Power Density (W/ft2) | Equipment Included in Power Density | Baseline Modeled Identically? |  | 0
Helpful Notes: | •All receptacle loads must be modeled identically between the Proposed and Baseline case and included in the simulations per Table G3.1#12 •Any credit for improved receptacle equipment must be submitted using the Exceptional Calculation Method |  |  |  | 1 2 3 | 0
0
0
0
0
0
0
Total | 0 | 0 | Total Power Modeled Using Space-by-Space Method (kW): | 0 | 1 2 | 0
0
0
Receptacle Equipment Power by Device | [5 empty] | 0
Equipment Type | Total Number in Project | Equipment Power per Device (Watts) | Typical Spaces Where Included | Baseline Modeled Identically? |  | 0
Helpful Notes: | •All receptacle loads must be modeled identically between the Proposed and Baseline case and included in the simulations per Table G3.1#12 •Any credit for improved receptacle equipment must be submitted using the Exceptional Calculation Method •Exception: When the process or receptacle equipment includes components regulated by minimum efficiency requirements in ASHRAE 90.1, these components may be modeled in the Baseline Case using the minimum ASHRAE 90.1 efficiencies, and in the proposed case using actual proposed case efficiencies (e.g. Baseline may be modeled using furnace efficiencies from Table 6.8.1E, boiler efficiencies from Table 6.8.1G, chiller efficiencies from Table 6.8.1C or Section 6.4.1.2, or motor efficiency from Section 10.4). |  |  |  | 1 2 3 | 0
0
0
0
0
0
0
Total | 0 | 0 | Total Power for Equipment Power Devices (kW): | 0 | 1 2 | 0
[5 empty] | 1 2 | 0
0
Other Process Equipment | [5 empty] | 1
Equipment Type (Change/Add Labels as Necessary) | Energy Source | Energy Demand (kW) | Modeling Parameters | Baseline Modeled Identically? |  | 1
Helpful Notes: | •All process loads must be modeled identically between the Proposed and Baseline case and included in the simulations per Table G3.1#12 •Any credit for improved process equipment must be submitted using the Exceptional Calculation Method •Exception: When the process or receptacle equipment includes components regulated by minimum efficiency requirements in ASHRAE 90.1, these components may be modeled in the Baseline Case using the minimum ASHRAE 90.1 efficiencies, and in the proposed case using actual proposed case efficiencies (e.g. Baseline may be modeled using furnace efficiencies from Table 6.8.1E, boiler efficiencies from Table 6.8.1G, chiller efficiencies from Table 6.8.1C or Section 6.4.1.2, or motor efficiency from Section 10.4). |  |  |  | 1 2 3 | 1
Elevators/Escalators | [5 empty] | 1
Refrigeration Equipment | [5 empty] | 1
Kitchen Equipment | [5 empty] | 1
Data Center Equipment | [5 empty] | 1
Process Exhaust Fans
1
1
Total |  | 0 | Total Power for Other Process Equipment (kW): | 0 | 1 2 | 1
[5 empty] | 1 2 | 1
|  |  | Total Power for Building Process/Receptacle Equipment(kW): | 0 |  | 1
1
Add an Equipment Type
Building Average Equipment Power Density (W/sq.ft.)
Space by Space Equipment Power Density (W/sq.ft.)
Equipment Power by Device (Watts)

## Service Water Heating
Table 1.4.5 - Service Water Heating
Instructions: Complete the Service Water Heaters table for each unique type of system in the project (required inputs are green). Use the Add a System Type button for more than one type of system. Complete the Service Hot Water Fixtures table if credit is modeled for low-flow fixtures in the Proposed case. If the project includes service hot water circulation pumps, complete the Service Hot Water Pumps table. An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". | [8 empty] | 1 2 3 4 5 6
Service Water Heaters
Model Input Parameter | Baseline Case |  |  |  | Proposed Case
Helpful Notes: | •New systems: minimum performance requirements from Table 7.8 per Table G3.1#11(b) •Existing systems: actual system inputs per Table G3.1#11(a) •Model separate service water heating system when design uses combined system with space heating per Table G3.1#11(e) •Condenser heat recovery as required by 6.5.6.2 per Table G3.1#11(f) |  |  |  | •Service water heaters modeled as designed (or installed) per Table G3.1#11(a&b) •Where no service hot water system exists or has been specified but the building will have service hot water loads, a service hot water system should be modeled identical to the Baseline per Table G3.1#11(c) •For buildings with no service hot water loads, no service hot water system should be modeled per Table G3.1#11(d) |  |  |  | 1 2 3 4 5 6 7
System Type & Fuel
Input Rating (kW, MBH, etc.)
Efficiency (EF, SL, %, etc.)
Storage Volume (gal)
Storage Temperature (°F)
Peak Hot Water Demand (gpm)
Condenser heat recovery
1 2
Service Hot Water Fixtures
Note: This table is only required to be completed if credit is modeled in the Proposed case for low-flow fixtures
Fixture Type | Fixture Outlet Temp (°F) | % Hot Water | Baseline Case |  |  | Proposed Case
|  |  | Flow Rate (gpm or gpc) | WEp1 Annual Total Water Consumption (kgal) | Annual Hot Water Consumption (kgal) | Flow Rate (gpm or gpc) | WEp1 Annual Total Water Consumption (kgal) | Annual Hot Water Consumption (kgal)
Helpful Notes: | •Refer to Table 3 in Chapter 50 of 2011 ASHRAE Handbook-HVAC Applications for fixture outlet temps used to determine % hot water •% Hot water should account for the DHW supply-to-fixture delta T, and for the percentage hot water versus cold water usage (e.g. residential lavatories would be expected to have cold water usage associated with brushing teeth) |  | •Fixtures included in the WEp1 calculations: values must be consistent with the WEp1 form •Additional fixtures not included in WEp1: use Proposed values or provide supporting documentation for Baseline assumption (example: Energy Star documentation of average hot water usage for residential dishwasher or clothes washer) |  |  | Values should be consistent with the design (or installed) fixtures and WEp1 (if applicable) |  |  | 1 2 3 4 5 6 7 8 9 10 11
Total
|  |  | Annual Equivalent Full Load Hours of DHW Operation |  |  | Annual Equivalent Full Load Hours of DHW Operation |  |  | 1 2
|  |  | Calculated Peak Hourly Flow (gal/hour) |  |  | Calculated Peak Hourly Flow (gal/hour) |  |  | 1 2
Service Hot Water Pumps
Model Input Parameter | Baseline Case |  |  |  | Proposed Case
Helpful Notes: | •Service hot water pumps should be modeled identically between the Proposed and Baseline case •Any credit for improved service hot water pumps must be submitted using the Exceptional Calculation Method |  |  |  | Service hot water pumps modeled as designed (or installed) |  |  |  | 1 2 3 4 5
Number of Pumps
Total Pump Power (kW)
Type of Pump (Constant/Variable)
Pump Control (Continuous/Scheduled)
Additional notes:
Add a Fixture Type
Add a System Type

## General HVAC
1
Table 1.4.6 - General HVAC | [6 empty] | 1
Instructions: Complete the Special Circumstances section, the Proposed and Baseline HVAC System Type(s) tables, and the HVAC Modeling Requirements checklist below. An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". | [5 empty] | 1 2 3 | 1
Special Circumstances |  |  |  | Yes | No | 1 2 | 1
Is the project building connected to a district or campus thermal energy system where thermal energy is produced for or distributed to multiple buildings? | [5 empty] | 1 2 | 1 |  | 0 | 0 | 0
| The district energy system includes (check all that apply): |  |  |  |  | 1 2 | FALSE | FALSE | FALSE
| Select how the district energy system has been modeled: Note: "DES v2" refers to the document "Treatment of District or Campus Thermal Energy in LEED V2 and LEED 2009 – Design & Construction" dated August 10, 2010, which can be accessed at http://www.usgbc.org/ShowFile.aspx?DocumentID=7671 |  |  |  |  | 1 2 3 4 5 6 7 8 | 0 | 0 | 0 | FALSE | FALSE | 0
| For DES v2 Option 2, identify the method for evaluating the district plant average efficiency. | [6 empty] | 0 | 0 |  | 0
Provide a narrative describing how the average efficiency was determined. Include information about how the thermal distribution losses and distribution pump energy was accounted for. If using the modeling method, upload summary simulation files or spreadsheet calculations as supporting documentation.
Please indicate all relevant equipment located on the project site: | [5 empty] | 1 2 |  | FALSE | FALSE | FALSE | FALSE | FALSE
|  |  |  | Yes | No | 1 2 | 1
Does the project building include tenant or other unfinished spaces whose systems (HVAC, lighting, etc.) are not included in the project's scope of work? | [5 empty] | 1 2 | 1 | 0 | 0 |  | 0
| Select how the unfinished spaces have been modeled: |  |  |  |  | 1 2 3 4 5 | 1 | 0 | 0 |  | 0
| Describe the energy efficiency measures modeled in the Proposed unfinished spaces (Note: signed tenant sales and lease agreements must be uploaded if using this option): |  |  |  |  | 1 2 3 | 0
Proposed HVAC System Type(s) | [5 empty] | 1 2 | 1 | 0 | :Non-default system selection
System Description |  |  | Spaces Modeled |  |  |  | 1
Helpful Notes: | •The HVAC system type and all related parameters, such as equipment capacities and efficiencies, must be modeled as designed (or installed) per Table G3.1#10(a&b) •Where no heating system exists or has been designed, the classification is assumed to be electric and the heating system is modeled identically to the Baseline case per Table G3.1#10(c) •Where no cooling system exists or has been designed, the cooling system is modeled identically to the Baseline case per Table G3.1#10(d) |  |  |  |  | 1 2 3 4 5 | 1
1
1
1
[6 empty] | 1 2 | 1
Baseline HVAC System Type(s) | [5 empty] | 1 2 | 1
Model Input Parameter | Table G3.1.1A System Type (or Semiconditioned System Description) | G3.1.1 Exception (or Semiconditioned Capacity and Area) | Spaces Modeled |  |  | 1 2 3 | 1
Helpful Notes: | •Refer to Section G3.1.1 and Table G3.1.1A (including footnotes) for Primary HVAC System selection •A system with any combination of fossil fuel and electric heat is considered fossil/electric hybrid •Systems 1-4: each thermal block shall be modeled with its own system •Systems 5-8: each floor shall be modeled with a separate system •Addendum dn added Systems 9 and 10 for heated only systems in certain spaces (e.g. storage rooms, stairwells, vestibules, electrical/mechanical rooms, parking garages, apparatus bays, and warehouses (see Addendum dn Section G3.1.1 Exceptions (e) and (f), and Tables (G3.1.1A and B)) •Additional system types for conditioned spaces only permitted using Exceptions to G3.1.1 (min 20,000 ft2 required for exception (a)) •Systems serving semiconditioned spaces should be modeled identically to the system in the Proposed case (see definition of space in Section 3.2 of ASHRAE 90.1 •For California Title-24 projects, type in the appropriate system type |  |  |  |  | 1 2 3 4 5 6 7 8 9 | 1
Primary HVAC System | - | [5 empty] | 1 | 0
Other HVAC System(s) | - | [5 empty] | 1 | 0
| - | [5 empty] | 1 | 0
[6 empty] | 1 2 | 1
HVAC Modeling Requirements | [5 empty] | 1 | 1
| Instructions: After completing the information above, click "Refresh Modeling Requirements" to the left. All Proposed and Baseline HVAC system types must be entered above to generate the correct modeling requirements below. After clicking "Refresh Modeling Requirements", identify each item as "Yes" or "No", and provide a further description for any items marked as "No". |  |  |  |  | 1 2 | 1
Proposed HVAC Requirements | All Proposed HVAC systems and related parameters, such as equipment capacities, efficiencies, airflows, fans, etc. have been modeled as designed and are consistent with supporting documentation uploaded in LEED Online |  |  |  |  | 1 2 | 1
| Each Proposed HVAC thermal zone has been modeled as a separate thermal block except as allowed by Table G3.1#7 |  |  |  |  | 1 | 1
| All Proposed HVAC systems serving conditioned spaces have been modeled with heating and cooling as required by Table G3.1#1(b), with heating and/or cooling added as necessary identically to the Baseline case per Table G3.1#10(c&d) except where System types (9) or (10) have been modeled in accordance with Addendum dn |  |  |  |  | 1 2 3 | 1
| All Proposed HVAC systems and related parameters can be modeled directly in the energy simulation program used |  |  |  |  | 1 | 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | DC 1 | DC 2 | DC 3 | DC 4 | DC 5 | DC 6 | DC 7 | DC 8 | DC 9 | DC 10 | DH 1 | DH 3 | DH 5 | DH 7 | DH 9 | DHC 1 | DHC 3 | DHC 5 | DHC 7 | DHC 9
| All Proposed fan part-load efficiency curves for variable volume fans have been modeled identically to the Baseline curves for variable volume fans (if not, provide a description of the fan curves used in the space at the bottom of this table, and confirm that the proposed case curves are representative of the actual building design) |  |  |  |  | 1 2 | 1 | System 1 - PTAC | System 2 - PTHP | System 3 - PSZ-AC | System 4 - PSZ-HP | System 5 - Packaged VAV with Reheat | System 6 - Packaged VAV with PFP Boxes | System 7 - VAV with Reheat | System 8 - VAV with PFP Boxes | System 9 - Heating and Ventilation | System 10 - Heating and Ventilation | System 1 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 2 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 3 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 4 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 5 (District Cooling) - Change to System 7 - VAV with Reheat | System 6 (District Cooling) - Change to System 8 - VAV with PFP Boxes | System 7 (District Cooling) - VAV with Reheat | System 8 (District Cooling)- VAV with PFP Boxes | System 9 - Heating and Ventilation | System 10 - Heating and Ventilation | System 1 (District Heating) - PTAC | System 3 (District Heating) - PSZ-AC with District Heating | System 5 (District Heating) - Packaged VAV with Reheat | System 7 (District Heating) - VAV with Reheat | System 9 (District Heating) - Heating and Ventilation | System 1 (District Heating & Cooling) - 4-pipe Fan Coil | System 3 (District Heating & Cooling) - 4-pipe CV AHU | System 5 (District Heating & Cooling) - Change to System 7 - VAV with Reheat | System 7 (Heating & Cooling) - VAV with Reheat | System 9 (District Heating) - Heating and Ventilation
Baseline Air-Side HVAC Requirements | All Baseline single zone systems (Systems 1-4) have been modeled with a separate HVAC system for each thermal block per G3.1.1 |  |  |  |  | 1 2 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  | 0 | 0
| All Baseline VAV systems (Systems 5-8) have been modeled with an HVAC system per floor, or one system per group of thermodynamically similar floors per G3.1.1 |  |  |  |  | 1 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  | 0 | 0
| All Baseline heating and ventilation systems (System 9 or 10) have been modeled with an HVAC system per floor per G3.1.1 except for Systems modeled using Addendum dn Exception G3.1.1(e) which have been modeled with an HVAC system per thermal zone |  |  |  |  | 1 2 3 | 0 | [8 empty] | 0 | 0 | [8 empty] | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 0
| All Baseline system cooling capacities auto-sized with 15% oversizing per G3.1.2.2 (at the system or plant level, but not both) |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| All Baseline system heating capacities auto-sized with 25% oversizing per G3.1.2.2 (at the system or plant level, but not both) |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| If the Proposed system has a preheat coil, it has been modeled and controlled in the same manner in the Baseline system per G3.1.2.3 |  |  |  |  | 1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| All Baseline supply and return fans operate continuously when spaces are occupied and cycle when unoccupied per G3.1.2.4 |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Demand control ventilation is modeled in the Baseline case for all spaces larger than 500 square feet that have a design occupancy for ventilation of greater than 40 people per 1,000 sf of floor area (except for spaces served by Baseline systems that do not have one of the following: an air-side economizer, automatic modulating control of the outdoor air damper, or a design outdoor airflow of greater than 3,000 cfm) per G3.1.2.5 / 6.4.3.9 |  |  |  |  | 1 2 3 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
| The minimum outdoor air ventilation rates (including infiltration) are the same for the Proposed and Baseline building designs consistent with Section G3.1.2.5 unless demand control ventilation is modeled for credit, in which case, the ASHRAE 62.1 minimum ventilation rates from IEQp1 are modeled for all Baseline systems where credit is taken for demand control ventilation |  |  |  |  | 1 2 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| All Baseline systems are modeled with zero outside airflow when fans are cycled to meet unoccupied setback temperatures |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| All Baseline supply airflows for Systems 1-8 have been auto-sized based on a 20°F supply-air-to-room-air cooling temperature difference (or the required ventilation/makeup air, whichever is greater) per G3.1.2.8 |  |  |  |  | 1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Baseline supply airflows for all heating and ventilation systems (System 9 or 10) have been auto-sized based on a 105°F supply air temperature (or the required ventilation/makeup air) per 90.1-2010 (as added by 90.1-2007 Addendum dn) |  |  |  |  | 1 2 | 0 | [8 empty] | 0 | 0 | [8 empty] | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 0
| All Baseline heat pumps modeled with electric auxiliary heat only energized below 40°F and as the last thermostat stage per G3.1.3.1 (compressor still enabled below 40°F). The compressor continues to operate in conjunction with the electric auxiliary heat as low as 17°F, in accordance with the Baseline equipment efficiency ratings from ASHRAE 90.1 Section 6.8. See ASHRAE Interpretation 90.1-2007-09 for more information |  |  |  |  | 1 2 3 4 | 0 |  | 0 |  | 0
| Where Baseline or Proposed efficiency ratings for DX cooling equipment, such as EER and COP, include fan energy, the descriptor is broken down into its components so that supply fan energy can be modeled separately. If the simulation program inputs are in units of EER or SEER, these descriptors are assumed to be broken out correctly. However, when the simulation program inputs are in other units such as COP or EIR (such as for the eQUEST detailed mode), these descriptors have been manually broken out at ARI‐rated conditions (external static pressure ranging from 0.2 in H20 to 0.75 in. H20 based on rated capacity, internal static pressures include the packaged unit with wet coil and no filters). The descriptors have not broken out using the modeled fan power. An acceptable method for breaking out the descriptor from its components is described in the EMIT User's Guide (www.rmi.org/Content/Files/EMIT%20User's%20Guide.pdf). | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0 | 0
| All Baseline VAV systems modeled with supply air temperature reset of 5°F under minimum cooling load conditions per G3.1.3.12 |  |  |  |  | 1 2 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  | 0 | 0
| All Baseline VAV reheat boxes modeled with a minimum flow setpoint of 0.4 cfm/sf (or minimum ventilation rate) per G3.1.3.13 |  |  |  |  | 1 | 0 |  |  |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 | [5 empty] | 0 | 0 |  |  |  | 0 | 0
| All Baseline fans in parallel VAV fan-powered boxes sized for 50% of peak primary airflow and modeled with 0.35 W/cfm fan power and a minimum flow setpoint of 30% of peak (or minimum ventilation rate) per G3.1.3.14 |  |  |  |  | 1 2 | 0 | [5 empty] | 0 |  | 0 | [7 empty] | 0 |  | 0
| All Baseline VAV fans (Systems 5-8) are modeled with VAV part-load performance curves consistent with Table G3.1.3.15 Method 1 or Method 2 |  |  |  |  | 1 2 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  | 0 | 0
| Fossil fuel is the only heating source reported in the Baseline simulation outputs, since the Baseline heating system(s) are fossil fuel heating systems |  |  |  |  | 1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Purchased heat is the only heating source reported in the Baseline simulation outputs, since the Baseline heating system(s) are purchased heat systems |  |  |  |  | 1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electricity is the only heating source reported in the Baseline simulation outputs, since the Baseline heating system(s) are electric heating systems |  |  |  |  | 1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline Water-Side HVAC Requirements | The Baseline boiler(s) have been modeled as natural draft per G3.1.3.2 |  |  |  |  | 1 | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0
| The Baseline hot water design supply temperature has been modeled as 180°F with a return temperature of 130°F (50°F ΔT) per G3.1.3.3 |  |  |  |  | 1 2 | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0
| The Baseline hot water supply temperature reset schedule has been modeled as 180°F at outdoor temperatures 20°F and below, 150°F at outdoor temperatures 50°F and above, and ramped linearly between 180°F and 150°F at outdoor temperatures between 20°F and 50°F per G3.1.3.4 |  |  |  |  | 1 2 3 | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0
| The Baseline hot water pump power has been modeled as 19 W/gpm per G3.1.3.5 |  |  |  |  | 1 | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Piping losses have not been modeled in the Baseline for hot or chilled water per G3.1.3.6 |  |  |  |  | 1 | 0 | 0 |  |  |  | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| The Baseline chilled water design supply temperature has been modeled as 44°F with a return temperature of 56°F (12°F ΔT) per G3.1.3.8 |  |  |  |  | 1 2 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
| The Baseline chilled water supply temperature reset schedule has been modeled as 44°F at outdoor temperatures 80°F and above, 54°F at outdoor temperatures 60°F and below, and ramped linearly between 44°F and 54°F at outdoor temperatures between 80°F and 60°F per G3.1.3.9 |  |  |  |  | 1 2 3 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
| The Baseline condenser water temperature reset schedule has been modeled to maintain a 70°F leaving water temperature where weather permits, floating up to a leaving water temperature at design conditions per G3.1.3.11 |  |  |  |  | 1 2 3 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
| The Baseline chilled water pump power has been modeled as 22 W/gpm per G3.1.3.10 |  |  |  |  | 1 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
| The Baseline cooling tower has been modeled with a two-speed axial fan per G3.1.3.11 with fan power per Table 6.8.1G |  |  |  |  | 1 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
| The Baseline condenser water supply temperature has been modeled as 85°F or 10°F approaching design wet-bulb temperature, whichever is lower, with a design temperature rise of 10°F per G3.1.3.11 |  |  |  |  | 1 2 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
| The Baseline cooling tower has been controlled to maintain a 70°F leaving water temperature where weather permits, floating up to leaving water temperature at design conditions per G3.1.3.11 |  |  |  |  | 1 2 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
| The Baseline condenser water pump power has been modeled as 19 W/gpm per G3.1.3.11 |  |  |  |  | 1 | 0 | [6 empty] | 0 | 0 | [15 empty] | 0
For each item entered as “No” above, describe the applicable ASHRAE 90.1 Appendix G exception(s) that apply, or the circumstances preventing the HVAC parameters from being modeled as required, or for proposed case parameters, details confirming that the proposed case model appropriately represents the actual building design. If the energy simulation software is not capable of modeling the required parameters, describe the adjustments that were made to provide a thermodynamically similar representation of the system or provide a narrative justifying why the predicted energy performance results will not be influenced: | [5 empty] | 1 2 3 4 | 1
[6 empty] | 1 2 3 | 1
1
1
1
1
1
1
1
1
1
1
1
1
Add an Other Baseline HVAC System
Add a Proposed HVAC System
Refresh Modeling Requirements
District Cooling
District Heating
CHP
ASHRAE 90.1-2007 Appendix G without Addenda
ASHRAE 90.1-2007 Appendix G Addendum ai
California Title-24 Baseline default efficiencies
DES v2 Option 1 (Building Stand-Alone)
DES v2 Option 2 (Aggregate Building/DES)
Modeling Method
Monitoring Method
Chillers
Cooling Towers / Fluid Coolers
Boilers for Space Heating / Backup Heat
Ground Source / Geothermal Heat Pump Loop
Combined Heat & Power (CHP)
All equipment in the unfinished spaces not included in the project scope of work has been modeled identically in the Baseline and Proposed case using the Baseline modeling requirements
Credit has been modeled in the Proposed case for energy efficiency measures that are specifically identified in signed tenant sales and lease agreements (LEED Core & Shell only. New Construction must be modeled identically in the Baseline and Proposed Case).

## Air-Side HVAC Details
Table 1.4.7A - Baseline Air-Side HVAC System Schedule | [6 empty] | Table 1.4.7B - Proposed Air-Side HVAC System Schedule
[14 empty] | 1 2 3 4 5 6 7 | 1 2 3 4 5 6 7
[14 empty] | 1 2 3 | 1 2
| Table 1.4.7A - Baseline Air-Side HVAC System Schedule | [6 empty] | Table 1.4.7B - Proposed Air-Side HVAC System Schedule | [5 empty] | 1 2 | [11 empty] | DC 1 | DC 2 | DC 3 | DC 4 | DC 5 | DC 6 | DC 7 | DC 8 | DC 9 | DC 10 | DH 1 | DH 3 | DH 5 | DH 7 | DH 9 | DHC 1 | DHC 3 | DHC 5 | DHC 7 | DHC 9
Model Input Parameter | Helpful Notes | HVAC System / Group |  | HVAC System / Group |  | Totals | Model Input Parameter | Helpful Notes | HVAC System / Group |  | HVAC System / Group |  | Totals | 1 |  | System 1 - PTAC | System 2 - PTHP | System 3 - PSZ-AC | System 4 - PSZ-HP | System 5 - Packaged VAV with Reheat | System 6 - Packaged VAV with PFP Boxes | System 7 - VAV with Reheat | System 8 - VAV with PFP Boxes | System 9 - Heating and Ventilation | System 10 - Heating and Ventilation | System 1 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 2 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 3 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 4 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 5 (District Cooling) - Change to System 7 - VAV with Reheat | System 6 (District Cooling) - Change to System 8 - VAV with PFP Boxes | System 7 (District Cooling) - VAV with Reheat | System 8 (District Cooling)- VAV with PFP Boxes | System 9 - Heating and Ventilation | System 10 - Heating and Ventilation | System 1 (District Heating) - PTAC | System 3 (District Heating) - PSZ-AC with District Heating | System 5 (District Heating) - Packaged VAV with Reheat | System 7 (District Heating) - VAV with Reheat | System 9 (District Heating) - Heating and Ventilation | System 1 (District Heating & Cooling) - 4-pipe Fan Coil | System 3 (District Heating & Cooling) - 4-pipe CV AHU | System 5 (District Heating & Cooling) - Change to System 7 - VAV with Reheat | System 7 (Heating & Cooling) - VAV with Reheat | System 9 (District Heating) - Heating and Ventilation
|  | Description | Units | Description | Units |  |  |  | Description | Units | Description | Units
*System Type | [6 empty] | *System Type | All inputs should be consistent with the Proposed energy model and the mechanical drawings and equipment schedules submitted in LEED Online | [5 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
System Designation(s) | Consistent with designations used in model | [5 empty] | System Designation(s) | [6 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Similar Systems | [6 empty] | Number of Similar Systems | [6 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Cooling Capacity | Auto-sized with 15% oversizing per G3.1.2.2 |  | kBtu/h |  | kBtu/h | 0 | Total Cooling Capacity |  |  | kBtu/h |  | kBtu/h | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*Table 6.8.1 Unitary Cooling Capacity Range | •Systems 1 & 2: Table 6.8.1D •Systems 3, 5, & 6: Table 6.8.1A •System 4: Table 6.8.1B •Systems 7-10: N/A |  | kBtu/h |  | kBtu/h | [8 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0 | 0
*Unitary Cooling Efficiency (EER or SEER) | Units should be consistent with the ASHRAE 90.1 minimum efficiency rating requirements for this system type | [5 empty] | *Unitary Cooling Efficiency | Units should be consistent with the ASHRAE 90.1 minimum efficiency rating requirements for this system type | [5 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0 | 0
*Unitary Cooling Part-load Efficiency (if applicable) | Enter N/A if not applicable | [5 empty] | *Unitary Cooling Part-load Efficiency | Indicate the part-load efficiency. Also describe the method for modeling part-load curves if the energy simulation does not have default curves for this equipment type. Enter N/A if not applicable. | [5 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0 | 0
Total Heating Capacity | Auto-sized with 25% oversizing per G3.1.2.2 |  | kBtu/h |  | kBtu/h | 0 | Total Heating Capacity | All inputs should be consistent with the Proposed energy model and the mechanical drawings and equipment schedules submitted in LEED Online |  | kBtu/h |  | kBtu/h | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*Table 6.8.1 Unitary Heating Capacity Range | •System 2: Table 6.8.1D •Systems 3 & 9: Table 6.8.1E •System 4: Table 6.8.1B •Systems 1, 5-8, 10: N/A |  | kBtu/h |  | kBtu/h | [8 empty] | 0 |  |  | 0 | 0 | 0 |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  |  |  |  | 0
*Unitary Heating Efficiency | List all relevant efficiencies (e.g. 3.2 COP at 47°F db/43°F wb, 2.0 COP at 17°F db/15°F wb outdoor air) | [5 empty] | *Unitary Heating Efficiency | List all relevant efficiencies (e.g. 3.2 COP at 47°F db/43°F wb, 2.0 COP at 17°F db/15°F wb outdoor air) | [5 empty] | 0 |  |  | 0 | 0 | 0 |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  |  |  |  | 0
*Fan Control | •Systems 1-4, 9 & 10: Constant Volume •Systems 5-8: Variable Volume | Constant Volume |  | Constant Volume |  |  | *Fan Control | e.g. Variable Speed Fans, 3-speed ECM fans with automated controls, constant speed, etc. | [5 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Supply Airflow | •Systems 1-8: Auto-sized based on 20°F ΔT •Systems 9-10: Auto-sized based on 105°F SAT |  | cfm |  | cfm | 0 | Supply Airflow | Inputs should be consistent with the mechanical drawings and equipment schedules submitted in LEED Online |  | cfm |  | cfm | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outdoor Airflow | •If DCV modeled in Proposed only: ASHRAE 62.1 minimum ventilation rates reported in IEQp1 •All other cases: identical to Proposed |  | cfm |  | cfm | 0 | Outdoor Airflow | Actual minimum outdoor airflow rates consistent with Mechanical Schedule |  | cfm |  | cfm | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand Control Ventilation | If required by Section 6.4.3.9 (spaces >500 sf with >40 people/1,000 sf) | [5 empty] | Demand Control Ventilation | Briefly describe how demand control ventilation was modeled | [5 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*Economizer High-Limit Shutoff (°F) | •Systems 1, 2, 9 & 10: N, A •Systems 3-8: as required by G3.1.2.6 & G3.1.2.7 by Climate Zone: • Not Required - 1a, 1b, 2a, 3a, 4a •75°F - 1b, 2b, 3b, 3c, 4b, 4c, 5b, 5c, 6b, 7b, 8 •70°F - 5a, 6a, 7a | Not Required |  | Not Required |  |  | *Economizer Control | Describe the type of economizer control and the high limit shutoff. Also indicate if the economizer controls are for less than 100% of the design supply air. |  | °F |  | °F |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
*Supply Air Temperature Reset | Systems 5-8: Supply air temperature reset of 5°F under minimum cooling load conditions per G3.1.3.12 (e.g. from 55 °F to 60 °F) | Not Required |  | Not Required |  |  | *Supply Air Temperature Reset | e.g. - Supply air temperature reset from 55°F to 62°F based on worst case zone | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  | 0 | 0
*Any individual systems with ≥5,000 cfm supply air and ≥70% outdoor air? | •Exhaust air energy recovery required for individual systems with ≥5,000 cfm supply air and ≥70% outdoor air per G3.1.2.10 unless any exceptions apply •50% energy recovery effectiveness •Bypass or control to permit economizer | [5 empty] | *Exhaust Air Energy Recovery | If the system includes energy recovery, describe the type of energy recovery and recovery effectiveness (example: enthalpy wheel - 75% effective). Otherwise, enter "N/A". | [5 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*Exhaust Air Energy Recovery Effectiveness or G3.1.2.10 Exception Claimed |  | N/A |  | N/A | [9 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Supply Fan Power | •Sum of fan power for all supply, return, relief, and exhaust fans cannot exceed G3.1.2.9 system fan power allowance calculated using supply cfm •Report exhaust fans not interlocked with HVAC operation (such as parking garage ventilation fans, or unconditioned electrical room exhaust fans), and exhaust fans not required in the calculations (such as fume hoods applying Exception 6.5.3.1.1, or kitchen hoods operating independently of the building HVAC system) in Table 1.4.4 |  | kW |  | kW |  | Supply Fan Power | •Report exhaust fans not interlocked with HVAC operation (such as parking garage ventilation fans, or unconditioned electrical room exhaust fans), and exhaust fans not required in the calculations (such as fume hoods applying Exception 6.5.3.1.1, or kitchen hoods operating independently of the building HVAC system) in Table 1.4.4 |  | kW |  | kW |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Return/Relief Fan Power |  |  | kW |  | kW |  | Return/Relief Fan Power |  |  | kW |  | kW |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust Fan Power |  |  | kW |  | kW |  | Exhaust Fan Power |  |  | kW |  | kW |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
System Fan Power |  | 0 | kW | 0 | kW | 0 | System Fan Power |  | 0 | kW | 0 | kW | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Allowed Fan Power: | These values are calculated based on, system type, any pressure adjustments listed below, the total supply volume, and the ASHRAE 90.1 fan motor efficiency associated with the fan bhp. | 0 | kW | 0 | kW | 0 | Other (Describe) | [6 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Total Table 6.5.3.1.1B Pressure Drop Adjustments (A). |  | 0 | bhp | 0 | bhp |  | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Pressure Drop Adjustments: (Systems 4 through 8) | •For each pressure adjustment allowed, enter the Baseline cfm through each device (CFMD) | cfm | in. w.c. | cfm | in. w.c. |  | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Fully ducted return and/or exhaust air systems | Adjustment = 0.5 in. w.c. | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Return and/or exhaust airflow control devices | only where modulated to maintain relative negative or positive space pressure (e.g. lab, operating room) | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Exhaust filters, scrubbers, or other exhaust treatment | Adjustment = Pressure drop of device calculated at fan system design condition | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Particulate Filtration Credit: MERV 9 through 12 | Adjustment = 0.5 in. w.c. | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Particulate Filtration Credit: MERV 13 through 15 | Adjustment = 0.9 in. w.c. | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters | Adjustment = Pressure drop calculated at 2× clean filter pressure drop at fan system design condition | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Carbon and other gas-phase air cleaners | Adjustment = Clean filter pressure drop at fan system design condition | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Heat recovery device | •only if modeled in Baseline per G3.1.2.10 •Adjustment = Pressure drop of device at fan system design condition | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Evaporative humidifier/cooler in series with another cooling coil | •only if modeled in Baseline • Adjustment = Clean filter pressure drop at fan system design condition | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Sound Attenuation Section | Adjustment = 0.15 in. w.c. | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Fume Hood Exhaust Exception | required if 6.5.3.1.1 Exception [c] is taken | [5 empty] | Other (Describe) | [6 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
* Non-mechanical cooling fan volume | For system types #9 and #10, if present in the proposed design, increases the baseline fan power allowance by 0.054 Watts/cfm. |  | cfm |  | cfm |  | Other (Describe) | [6 empty] | 0 | [9 empty] | 0 | 0 | [8 empty] | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 0
*See Instructions above | [6 empty] | *See Instructions above
HeatingOnly |  | TRUE | 1 | TRUE | 1 | 1
NotHeatingOnly |  | TRUE | 1 | TRUE | 1 | 1
UnitaryCooling |  | TRUE | 1 | TRUE | 1 | 1
UnitaryHeating |  | TRUE | 1 | TRUE | 1 | 1
No Pressure Adjustment |  | TRUE | 1 | TRUE | 1 | 1
No Economizer |  | TRUE | 1 | TRUE | 1 | 1
UnitaryHeatingSize |  | TRUE | 1 | TRUE | 1 | 1
SATreset |  | TRUE | 1 | TRUE | 1 | 1
Instructions: Enter all applicable input parameters for the Baseline air-side HVAC systems below. All systems included in the model should be entered. Each individual system may be entered separately, or multiple systems may be grouped together if all input parameters identified with an (*) are similar. The table is set up for two unique HVAC systems (or two groups of similar systems), and additional systems (or groups of similar systems) should be added as necessary using the Add a System button. An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A".
Note: All Baseline systems must be identified in the General HVAC Tab in order to display the relevant Baseline building inputs below. If General HVAC system types are changed, system types must be reselected in this tab.
Instructions: Instructions: Enter all applicable input parameters for the Proposed air-side HVAC systems below. All systems included in the model should be entered. Each individual system may be entered separately, or multiple systems may be grouped together if all input parameters identified with an (*) are similar. The table is set up for two unique HVAC systems (or two groups of similar systems), and additional systems (or groups of similar systems) should be added as necessary using the Add a System button. An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A".
Add a System
Add a System
Print Baseline and Proposed Air-Side HVAC System Schedules
Print Baseline and Proposed Air-Side HVAC System Schedules

## Water-Side HVAC Details
[9 empty] | Non-default System Selection: | 0 |  |  |  | TOTALS: | Purchased | Baseline Applies? | System 1 - PTAC | System 2 - PTHP | System 3 - PSZ-AC | System 4 - PSZ-HP | System 5 - Packaged VAV with Reheat | System 6 - Packaged VAV with PFP Boxes | System 7 - VAV with Reheat | System 8 - VAV with PFP Boxes | System 9 - Heating and Ventilation | System 10 - Heating and Ventilation | System 1 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 2 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 3 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 4 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 5 (District Cooling) - Change to System 7 - VAV with Reheat | System 6 (District Cooling) - Change to System 8 - VAV with PFP Boxes | System 7 (District Cooling) - VAV with Reheat | System 8 (District Cooling)- VAV with PFP Boxes | System 1 (District Heating) - PTAC | System 3 (District Heating) - PSZ-AC with District Heating | System 5 (District Heating) - Packaged VAV with Reheat | System 7 (District Heating) - VAV with Reheat | System 9 (District Heating) - Heating and Ventilation | System 1 (District Heating & Cooling) - 4-pipe Fan Coil | System 3 (District Heating & Cooling) - 4-pipe CV AHU | System 5 (District Heating & Cooling) - Change to System 7 - VAV with Reheat | System 7 (Heating & Cooling) - VAV with Reheat | System 9 (District Heating) - Heating and Ventilation | Proposed Applies | Proposed Model | Proposed District ai or Option 1
| Table 1.4.8 - Water-Side HVAC System Schedule | [11 empty] | HHW | 0 | 0 | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| Instructions: Enter all applicable input parameters for the Baseline and Proposed water-side HVAC systems below. All systems included in the model should be entered. An example of the expected level of detail has been provided for each input. Please refer to the Helpful Notes for information about Appendix G modeling protocol. For any information not applicable to the project, simply enter "N/A". If taking credit for a campus or district plant efficiency using the DES v2 Option 2 Guidance, please include all relevant information regarding the District Plant equipment in the Proposed Case. For projects using the DES v2 Option 2 Guidance Option 1, or ASHRAE 90.1 Addendum ai for district energy systems, it is recommended that the Proposed Case inputs be completed first, and the description for many Baseline Case inputs will be auto-generated based on the proposed case inputs. Baseline Helpful notes relevant to DES v2 Option 1 and ASHRAE 90.1 Addendum ai are abbreviated as "DESv2#1" and "ai" respectively. | [5 empty] | 1 2 3 4 | Show/Hide | Applicable Baseline | Applicable Proposed | Purchased | DES Option 2 | CHW | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[13 empty] | CW | 0 |  | 0 | [6 empty] | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
Model Input Parameter |  | Baseline Helpful Notes | Baseline Case | Units | Proposed Case | Units | 1 |  |  |  | CHW | District Cooling | CHP | 0 |  | 0 | [29 empty] | 0
Chilled Water | Number and Type of Chillers (and capacity per chiller if more than one type or size of chiller) | •≤300 tons building peak: 1 water-cooled screw chiller •300-600 tons building peak: 2 equally-sized water-cooled screw chillers •≥600 tons building peak: At least 2 water-cooled centrifugal chillers (800 tons max per chiller) | [5 empty] | 0 | 0 | 0 | No | No |  |  |  | 0 | [28 empty] | 0
[8 empty] | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Purchased Chilled Water Rate (Cost per Unit Energy) | Describe how the purchased chilled water rate was determined. Local purchased energy rates must be used when available; when not available, the rates must account for the total costs associated with maintaining the district equipment, and generating and delivering the energy to the project site | N/A |  | N/A |  |  | 0 | 0 | 0 | [34 empty] | 0
| Total Chiller Capacity | Auto-sized with 15% oversizing (unless oversized at the system coil) per G3.1.2.2 | N/A | tons | N/A | tons |  | 0 | 0 | 0 | Proposed Purchased CHW |  |  |  |  | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Chiller Efficiency - Full Load | Per Table 6.8.1C efficiencies | N/A |  | N/A |  |  | 0 | 0 | 0 | No |  |  |  |  | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Chiller Efficiency - Part Load |  | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Chilled Water (CHW) Supply Temp | 44°F per G3.1.3.8 | N/A | °F | N/A | °F |  | 0 | 0 | 0 | Proposed Purchased Heat |  |  |  |  | 0 | [28 empty] | 0
| CHW ΔT | 12°F per G3.1.3.8 | N/A | °F | N/A | °F |  | 0 | 0 | 0 | No |  |  |  |  | 0 | [28 empty] | 0
| CHW Supply Temp Reset Parameters | 44°F at outdoor temps 80°F and above, 54°F at outdoor temps 60°F and below, and ramped linearly between 44°F and 54°F at outdoor temps between 80°F and 60°F per G3.1.3.9 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHW Loop Configuration | Primary/secondary per G3.1.3.10 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Number of Primary CHW Pumps | 1 per chiller per G3.1.3.11 | N/A | # | N/A | # |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Primary CHW Pump Power | 22 W/gpm total for the system per G3.1.3.10 - 11 W/gpm assumed for Primary pumps which can be overrideen to match proposed primary/secondary percentages if proposed case has primary/secondary CHW pumps | N/A |  | N/A | W/gpm |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Primary CHW Pump Flow | Auto-sized with a capacity ratio of 1.0 based on CHW temperatures | N/A | gpm | N/A | gpm |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Primary CHW Pump Control | Constant Flow - each primary pump interlocked to operate with associated chiller - G3.1.3.10, G3.1.3.11 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Number of Secondary CHW Pumps | 1 per G3.1.3.10 | N/A | # | N/A | # |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Secondary CHW Pump Power | 22 W/gpm total for the system per G3.1.3.10 - 11 W/gpm assumed for secondary pumps which can be overrideen to match proposed primary/secondary percentages if proposed case has primary/secondary CHW pumps | N/A | W/gpm | N/A | W/gpm |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Secondary CHW Pump Flow | Auto-sized with a capacity ratio of 1.0 based on CHW temperatures | N/A | gpm | N/A | gpm |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Secondary CHW Pump Control | <300 tons: riding the pump curve ≥300 tons: variable speed | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Water-Side Economizer | Not required | Not required |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Water-Side Energy Recovery | Not required | Not required |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
[8 empty] | 1 | 1 | 1
Cooling Tower & Condenser Water | Number of Cooling Towers / Fluid Coolers | 1 per G3.1.3.11 | N/A | # | N/A | # |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Cooling Tower Fan Power | Minimum 38.2 gpm/hp (maximum 0.0262 hp/gpm or 19.5 W/gpm) per Table 6.8.1G | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Cooling Tower Fan Control | Two-speed axial fans per G3.1.3.11 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Condenser Water (CW) Leaving Temp | 85°F or 10°F approaching design wet-bulb temperature, whichever is lower per G3.1.3.11 | N/A | °F | N/A | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| CW ΔT | 10°F per G3.1.3.11 | N/A | °F | N/A | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| CW Loop Temp Reset Parameters | Maintain a 70°F leaving water temperature where weather permits, floating up to leaving water temperature at design conditions per G3.1.3.11 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| Number of CW Pumps | 1 per chiller per G3.1.3.11 | N/A | # | N/A | # |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| CW Pump Power | 19 W/gpm per G3.1.3.11 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| CW Pump Flow | Auto-sized with a capacity ratio of 1.0 based on CW temperatures | N/A | gpm | N/A | gpm |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
| CW Pump Control | Riding the pump curve per G3.1.3.11 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [6 empty] | 0 | 0 | [13 empty] | 0 | [6 empty] | 0
[8 empty] | 1 | 1 | 1
Geothermal Loop | Type of Geothermal system | Proposed Case: Describe the geothermal or geoexchange system (e.g. closed loop vertical system, 4 inch diameter drilled 20 feet apart, 250 feet deep) | N/A | N/A |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Soil Conductivity (if applicable) | Not required | N/A | N/A |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geothermal source design temperature - summer | Not required | N/A | N/A |  | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geothermal source design temperature - winter | Not required | N/A | N/A |  | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geoexchange loop design fluid supply temperature - cooling | Not required | N/A | N/A |  | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geoexchange loop design fluid supply temperature -heating | Not required | N/A | N/A |  | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geoexchange loop - operating temperature | Not required | N/A | N/A |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geothermal energy transfer effect | Not required | N/A | N/A |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geothermal Loop Pumping Configuration | Not required | N/A | N/A |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Number of Geothermal Loop Pumps | Not required | N/A | N/A |  | # |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geothermal Loop Pump Control | Not required | N/A | N/A |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geothermal Pump Power | Not required | N/A | N/A |  | W/gpm |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Geothermal Loop Flow | Not required | N/A | N/A |  | gpm |  | 0 | 0 | 0 | Purchased | DES Option 2 |  |  |  | 0 | [28 empty] | 0
| Geothermal Air-side Efficiency curves | Not required | N/A | N/A |  |  |  | 0 | 0 | 0 | HW | District Heating |  |  |  | 0 | [28 empty] | 0
[8 empty] | 1 | 1 | 1
Hot Water / Steam | Number and Type of Boilers | ≤15,000 sf: 1 natural draft hot water boiler >15,000 sf: 2 equally-sized natural draft hot water boilers staged as required by the load |  |  | N/A |  |  | 0 | 0 | 0 | No | No |  |  |  | 0 | [28 empty] | 0
| Purchased Heating Rate (Cost per unit energy) | Describe how the purchased heating rate was determined. Local purchased energy rates must be used when available; when not available, the rates must account for the total costs associated with maintaining the district equipment, and generating and delivering the energy to the project site | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Boiler Capacity | Auto-sized with 25% oversizing (unless oversized at the system coil) per G3.1.2.2 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 | [11 empty] | 0
| Boiler Efficiency | Per Table 6.8.1F minimum efficiencies | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 | [11 empty] | 0
| Hot Water or Steam (HHW) Supply Temp | 180°F per G3.1.3.3 | N/A | °F | N/A | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| HHW ΔT | 50°F per G3.1.3.3 | N/A | °F | N/A | °F |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| HHW Temp Reset Parameters | 180°F at outdoor temps 20°F and below, 150°F at outdoor temps 50°F and above, and ramped linearly between 180°F and 150°F at outdoor temps between 20°F and 50°F per G3.1.3.4 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| HHW Loop Configuration | Primary-only per G3.1.3.5 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Number of Primary HHW Pumps | One pump | N/A | # | N/A | # |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Primary HHW Pump Power | 19 W/gpm per G3.1.3.5 | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Primary HHW Pump Flow | Auto-sized with a capacity ratio of 1.0 based on HHW temperatures | N/A | gpm | N/A | gpm |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Primary HHW Pump Control | <120,000 sf: riding the pump curve ≥120,000 sf: variable speed | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Number of Secondary HHW Pumps | N/A (Baseline is primary-only) | N/A | # | N/A | # |  | 0 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 | [11 empty] | 0
| Secondary HHW Pump Power | N/A (Baseline is primary-only) | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 | [11 empty] | 0
| Secondary HHW Pump Flow | N/A (Baseline is primary-only) | N/A |  | N/A | gpm |  | 0 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 | [11 empty] | 0
| Secondary HHW Pump Control | N/A (Baseline is primary-only) | N/A |  | N/A |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 | 0 |  |  | 0 |  | 0 | [11 empty] | 0
[8 empty] | 1 | 1 | 1
Combined Heat & Power (CHP) | CHP: Type of generator |  | N/A |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Quantity of CHP generators |  | N/A |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| Total capacity of CHP generators (kW) at design conditions |  | N/A |  |  | kW |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHP: Thermal efficiency (%) at design conditions |  | N/A |  |  | % |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHP: Electrical efficiency (%) at design conditions |  | N/A |  |  | % |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHP: Controls / Schedule |  | N/A |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHP: Fuel Source |  | N/A |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHP: Where is the recovered heat used? (e.g. gas absorption chillers, hot water distribution loop, etc.) |  | N/A |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHP: Backup heat source when waste heat from CHP is unavailable? (e.g. fossil fuel boilers) |  | N/A |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
| CHP: Parasitic losses (e.g. air handling unit to cool the intake air) |  | N/A |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [28 empty] | 0
[8 empty] | 1 | 1 | 1
| Other (Describe) | [6 empty] | 1 | 1 | 1 | [5 empty] | 1 | [28 empty] | 1
| Other (Describe) | [6 empty] | 1 | 1 | 1 | [5 empty] | 1 | [28 empty] | 1
| Other (Describe) | [6 empty] | 1 | 1 | 1 | [5 empty] | 1 | [28 empty] | 1
| Other (Describe) | [6 empty] | 1 | 1 | 1 | [5 empty] | 1 | [28 empty] | 1
| Other (Describe) | [6 empty] | 1 | 1 | 1 | [5 empty] | 1 | [28 empty] | 1
| Other (Describe) | [6 empty] | 1 | 1 | 1 | [5 empty] | 1 | [28 empty] | 1
1
1
Show Water-side Inputs Based on General HVAC Selections

## Lighting Lookup (hidden)
Building Area Method Categories | Table 9.5.1 LPD (W/sf) | Space by Space Categories | Table 9.6.1 LPD (W/sf) | Exterior Categories | Table 9.4.5 LPD (W/sf or W/lf) | Tradable?
Automotive facility | 0.9 | Office-Enclosed | 1.1 | Parking lots and drives | 0.15 | Yes | Area
Convention center | 1.2 | Office-Open Plan | 1.1 | Walkways less than 10 ft wide | 1 | Yes | Length
Courthouse | 1.2 | Conference/Meeting/Multipurpose | 1.3 | Walkways 10 ft wide or greater | 0.2 | Yes | Area
Dining: bar lounge/leisure | 1.3 | Classroom/Lecture/Training | 1.4 | Plaza areas | 0.2 | Yes | Area
Dining: cafeteria/fast food | 1.4 | Classroom/Lecture/Training-Penitentiary | 1.3 | Special feature areas | 0.2 | Yes | Area
Dining: family | 1.6 | Lobby | 1.3 | Stairways | 1 | Yes | Area
Dormitory | 1 | Lobby-Hotel | 1.1 | Main entries | 30 | Yes | Length
Exercise center | 1 | Lobby-Performing Arts Theater | 3.3 | Other doors | 20 | Yes | Length
Gymnasium | 1.1 | Lobby-Motion Picture Theater | 1.1 | Canopies (free standing and attached and overhangs) | 1.25 | Yes | Area
Health-care clinic | 1 | Audience/Seating Area | 0.9 | Open sales areas (including vehicle sales lots) | 0.5 | Yes | Area
Hospital | 1.2 | Audience/Seating Area-Gymnasium | 0.4 | Street frontage for vehicle sales lots | 20 | Yes | Length
Hotel | 1 | Audience/Seating Area-Exercise Center | 0.3
Library | 1.3 | Audience/Seating Area-Convention Center | 0.7
Manufacturing facility | 1.3 | Audience/Seating Area-Penitentiary | 0.7
Motel | 1 | Audience/Seating Area-Religious Buildings | 1.7
Motion picture theater | 1.2 | Audience/Seating Area-Sports Arena | 0.4
Multifamily | 0.7 | Audience/Seating Area-Performing Arts Theater | 2.6
Museum | 1.1 | Audience/Seating Area-Motion Picture Theater | 1.2
Office | 1 | Audience/Seating Area-Transportation | 0.5
Parking garage | 0.3 | Atrium-First Three Floors | 0.6
Penitentiary | 1 | Atrium-Each Additional Floor | 0.2
Performing arts theater | 1.6 | Lounge/Recreation | 1.2
Police/fire station | 1 | Lounge/Recreation-Hospital | 0.8
Post office | 1.1 | Dining Area | 0.9
Religious building | 1.3 | Dining Area-Penitentiary | 1.3
Retail | 1.5 | Dining Area-Hotel | 1.3
School/university | 1.2 | Dining Area-Motel | 1.2
Sports arena | 1.1 | Dining Area-Bar Lounge/Leisure Dining | 1.4
Town hall | 1.1 | Dining Area-Family Dining | 2.1
Transportation | 1 | Food Preparation | 1.2
Warehouse | 0.8 | Laboratory | 1.4
Workshop | 1.4 | Restrooms | 0.9
|  | Dressing/Locker/Fitting Room | 0.6
|  | Corridor/Transition | 0.5
|  | Corridor/Transition-Hospital | 1
|  | Corridor/Transition-Manufacturing Facility | 0.5
|  | Stairs-Active | 0.6
|  | Active Storage | 0.8
|  | Active Storage-Hospital | 0.9
|  | Inactive Storage | 0.3
|  | Inactive Storage-Museum | 0.8
|  | Electrical/Mechanical | 1.5
|  | Workshop | 1.9
|  | Sales Area | 1.7
|  | Gymnasium/Exercise Center-Playing Area | 1.4
|  | Gymnasium/Exercise Center-Exercise Area | 0.9
|  | Courtroom | 1.9
|  | Confinement Cells | 0.9
|  | Judges' Chambers | 1.3
|  | Fire Stations-Engine Room | 0.8
|  | Fire Stations-Sleeping Quarters | 0.3
|  | Post Office-Sorting Area | 1.2
|  | Convention Center-Exhibit Space | 1.3
|  | Library-Card File and Cataloging | 1.1
|  | Library-Stacks | 1.7
|  | Library-Reading Area | 1.2
|  | Hospital-Emergency | 2.7
|  | Hospital-Recovery | 0.8
|  | Hospital-Nurses' Station | 1
|  | Hospital-Exam/Treatment | 1.5
|  | Hospital-Pharmacy | 1.2
|  | Hospital-Patient Room | 0.7
|  | Hospital-Operating Room | 2.2
|  | Hospital-Nursery | 0.6
|  | Hospital-Medical Supply | 1.4
|  | Hospital-Physical Therapy | 0.9
|  | Hospital-Radiology | 0.4
|  | Hospital-Laundry Washing | 0.6
|  | Automotive-Service/Repair | 0.7
|  | Manufacturing-Low Bay (<25 ft Floor to Ceiling Height) | 1.2
|  | Manufacturing-High Bay (≥25 ft Floor to Ceiling Height) | 1.7
|  | Manufacturing-Detailed Manufacturing | 2.1
|  | Manufacturing-Equipment Room | 1.2
|  | Manufacturing-Control Room | 0.5
|  | Hotel/Motel Guest Rooms | 1.1
|  | Dormitory-Living Quarters | 1.1
|  | Museum-General Exhibition | 1
|  | Museum-Restoration | 1.7
|  | Bank/Office-Banking Activity Area | 1.5
|  | Religious Buildings-Worship Pulpit, Choir | 2.4
|  | Religious Buildings-Fellowship Hall | 0.9
|  | Retail-Sales Area | 1.7
|  | Retail-Mall Concourse | 1.7
|  | Sports Arena-Ring Sports Area | 2.7
|  | Sports Arena-Court Sports Area | 2.3
|  | Sports Arena-Indoor Playing Field Area | 1.4
|  | Warehouse-Fine Material Storage | 1.4
|  | Warehouse-Medium/Bulky Material Storage | 0.9
|  | Parking Garage-Garage Area | 0.2
|  | Transportation-Airport-Concourse | 0.6
|  | Transportation-Air/Train/Bus-Baggage Area | 1
|  | Transportation-Terminal-Ticket Counter | 1.5

## HVAC Lookup (hidden)
District Cooling | 0
District Heating | 0
ASHRAE 90.1-2007 without Addenda | 0
ASHRAE 90.1-2007 with Addendum ai | 0
California Title-24 Baseline default efficiencies | 0
DES v2 Option 1 | 0
DES v2 Option 2 | 0
|  | 1 | FALSE | FALSE | FALSE | 0 | [7 empty] | Fully ducted return and/or exhaust air systems | 0.5 | in. w.c. | Motor Horsepower Nominal Efficiency Based on ASHRAE 90.1-2007 Table 10.8 |  |  | Climate Zone | Economizer Shutoff Temp for Systems 3 through 8
|  | •No DES •ASHRAE 90.1-2007 Appendix G without Addenda •DES v2 Option 1 | •ASHRAE 90.1-2007 Appendix G with Addendum ai •DES v2 Option 2 •District Cooling Only | •ASHRAE 90.1-2007 Appendix G with Addendum ai •DES v2 Option 2 •District Heating Only | •ASHRAE 90.1-2007 Appendix G with Addendum ai •DES v2 Option 2 •District Cooling and Heating | California Title-24 Baseline default efficiencies | Fan Power per cfm | Multiplier X A | Multiplier x motor efficiency | Multiplier x Non-mechanical cooling | kBtu/h | (British thermal unit per hour) x 1,000 | 1 | Return and/or exhaust airflow control devices | 0.5 | in. w.c. | Motor Horsepower | Min. Nominal Full-load Efficiency* | Next Motor Size Up HP | 1A | Not Required
System 1 - PTAC | 1 | System 1 - PTAC | System 1 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 1 (District Heating) - PTAC | System 1 (District Heating & Cooling) - 4-pipe Fan Coil | Describe the California Title-24 Baseline System Type | 0.0003 | 0 | 0 | 0 | tons | tons | 12 | Exhaust filters, scrubbers or other exhaust treatment | Enter pressure drop of device calculated at fan system design conditions | in. w.c. | 0 |  | 82.5% | 1B | Not Required
System 2 - PTHP | 2 | System 2 - PTHP | System 2 (District Cooling) - 4-pipe Fan Coil with HW Boiler |  |  |  | 0.0003 | 0 | 0 | 0 | kW | Kilowatt | 3.412 | Particulate Filtration Credit: MERV 9 through 12 | 0.5 | in. w.c. | 1 | 82.5% | 84% | 2A | Not Required
System 3 - PSZ-AC | 3 | System 3 - PSZ-AC | System 3 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 3 (District Heating) - PSZ-AC with District Heating | System 3 (District Heating & Cooling) - 4-pipe CV AHU |  | 0.00094 | 1 | 1 | 0 | Btuh | British thermal unit per hour | 0.001 | Particulate Filtration Credit: MERV 13 through 15 | 0.9 | in. w.c. | 1.5 | 84% | 84% | 2B | 75
System 4 - PSZ-HP | 4 | System 4 - PSZ-HP | System 4 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace |  |  |  | 0.00094 | 1 | 1 | 0 |  |  |  | Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters | Enter pressure drop calculated at 2× clean filter pressure drop at fan system design condition | in. w.c. | 2 | 84% | 87.5% | 3A | Not Required
System 5 - Packaged VAV with Reheat | 5 | System 5 - Packaged VAV with Reheat | System 5 (District Cooling) - Change to System 7 - VAV with Reheat | System 5 (District Heating) - Packaged VAV with Reheat | System 5 (District Heating & Cooling) - Change to System 7 - VAV with Reheat |  | 0.0013 | 1 | 1 | 0 |  |  |  | Carbon and other gas-phase air cleaners | Enter clean filter pressure drop at fan system design condition | in. w.c. | 3 | 87.5% | 87.5% | 3B | 75
System 6 - Packaged VAV with PFP Boxes | 6 | System 6 - Packaged VAV with PFP Boxes | System 6 (District Cooling) - Change to System 8 - VAV with PFP Boxes |  |  |  | 0.0013 | 1 | 1 | 0 |  |  |  | Heat recovery device | Pressure drop of device at fan system design condition | in. w.c. | 5 | 87.5% | 89.5% | 3C | 75
System 7 - VAV with Reheat | 7 | System 7 - VAV with Reheat | System 7 (District Cooling) - VAV with Reheat | System 7 (District Heating) - VAV with Reheat | System 7 (Heating & Cooling) - VAV with Reheat |  | 0.0013 | 1 | 1 | 0 |  |  |  | Evaporative humidifier/cooler in series with another cooling coil | Pressure drop of device at fan system design condition | in. w.c. | 7.5 | 89.5% | 89.5% | 4A | Not Required
System 8 - VAV with PFP Boxes | 8 | System 8 - VAV with PFP Boxes | System 8 (District Cooling)- VAV with PFP Boxes |  |  |  | 0.0013 | 1 | 1 | 0 |  |  |  | Sound Attenuation Section | 0.15 | in. w.c. | 10 | 89.5% | 91% | 4B | 75
System 9 - Heating and Ventilation | 9 | System 9 - Heating and Ventilation | System 9 - Heating and Ventilation | System 9 (District Heating) - Heating and Ventilation | System 9 (District Heating) - Heating and Ventilation |  | 0.0003 | 0 | 0 | 5.4e-05 |  |  |  | Fume hood Exhaust Exception | -1 | in. w.c. | 15 | 91% | 91% | 4C | 75
System 10 - Heating and Ventilation | 10 | System 10 - Heating and Ventilation | System 10 - Heating and Ventilation |  |  |  | 0.0003 | 0 | 0 | 5.4e-05 | [6 empty] | 20 | 91% | 92.4% | 5A | 70
| 1 |  | System 1 - PTAC | System 1 - PTAC | System 1 - PTAC |  | 0.0003 | 0 | 0 | 0 | [6 empty] | 25 | 92.4% | 92.4% | 5B | 75
| 2 |  | System 2 - PTHP | System 2 - PTHP | System 2 - PTHP |  | 0.0003 | 0 | 0 | 0 | [6 empty] | 30 | 92.4% | 93% | 5C | 75
| 3 |  | System 3 - PSZ-AC | System 3 - PSZ-AC | System 3 - PSZ-AC |  | 0.00094 | 1 | 1 | 0 | [6 empty] | 40 | 93% | 93% | 6A | 70
| 4 |  | System 4 - PSZ-HP | System 4 - PSZ-HP | System 4 - PSZ-HP |  | 0.00094 | 1 | 1 | 0 | [6 empty] | 50 | 93% | 93.6% | 6B | 75
| 5 |  | System 5 - Packaged VAV with Reheat | System 5 - Packaged VAV with Reheat | System 5 - Packaged VAV with Reheat |  | 0.0013 | 1 | 1 | 0 | [6 empty] | 60 | 93.6% | 94.1% | 7A | 70
| 6 |  | System 6 - Packaged VAV with PFP Boxes | System 6 - Packaged VAV with PFP Boxes | System 6 - Packaged VAV with PFP Boxes |  | 0.0013 | 1 | 1 | 0 | [6 empty] | 75 | 94.1% | 94.5% | 7B | 75
| 7 |  | System 7 - VAV with Reheat | System 7 - VAV with Reheat | System 7 - VAV with Reheat |  | 0.0013 | 1 | 1 | 0 | [6 empty] | 100 | 94.5% | 94.5% | 8 | 75
| 8 |  | System 8 - VAV with PFP Boxes | System 8 - VAV with PFP Boxes | System 8 - VAV with PFP Boxes |  | 0.0013 | 1 | 1 | 0 | [6 empty] | 125 | 94.5% | 95%
| 9 |  |  | System 9 - Heating and Ventilation | System 9 - Heating and Ventilation |  | 0.0003 | 0 | 0 | 5.4e-05 | [6 empty] | 150 | 95% | 95%
| 10 |  |  | System 10 - Heating and Ventilation | System 10 - Heating and Ventilation |  | 0.0003 | 0 | 0 | 5.4e-05 | [6 empty] | 200 | 95% | 95%
*Note: Values provided for enclosed motors @ 1800 rpm as specified in ASHRAE 90.1-2007 Appendix G, Section G3.1.2.9
|  | Unitary Cooling | Unitary Heating | No Pressure Adjustment | HeatingOnly | UnitaryHeatingSize | NoEconomizer | SATreset
|  | System 1 - PTAC | System 2 - PTHP | System 1 - PTAC | System 9 - Heating and Ventilation | System 3 - PSZ-AC | System 1 - PTAC | System 5 - Packaged VAV with Reheat
|  | System 2 - PTHP | System 3 - PSZ-AC | System 1 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 10 - Heating and Ventilation | System 4 - PSZ-HP | System 1 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 5 (District Cooling) - Change to System 7 - VAV with Reheat
|  | System 3 - PSZ-AC | System 3 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 1 (District Heating) - PTAC | System 9 (District Heating) - Heating and Ventilation | System 9 - Heating and Ventilation | System 1 (District Heating) - PTAC | System 5 (District Heating) - Packaged VAV with Reheat
|  | System 4 - PSZ-HP | System 4 - PSZ-HP | System 1 (District Heating & Cooling) - 4-pipe Fan Coil |  | System 10 - Heating and Ventilation | System 1 (District Heating & Cooling) - 4-pipe Fan Coil | System 5 (District Heating & Cooling) - Change to System 7 - VAV with Reheat
|  | System 5 - Packaged VAV with Reheat | System 4 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 1 (District Heating) - PTAC |  | System 3 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 2 - PTHP | System 6 - Packaged VAV with PFP Boxes
|  | System 6 - Packaged VAV with PFP Boxes | System 9 - Heating and Ventilation | System 1 (District Heating & Cooling) - 4-pipe Fan Coil |  | System 4 (District Cooling) - 2-pipe CV AHU with Fossil Fuel Furnace | System 2 (District Cooling) - 4-pipe Fan Coil with HW Boiler | System 6 (District Cooling) - Change to System 8 - VAV with PFP Boxes
|  | System 1 (District Heating) - PTAC |  | System 2 - PTHP |  |  | System 9 - Heating and Ventilation | System 7 - VAV with Reheat
|  | System 3 (District Heating) - PSZ-AC with District Heating |  | System 2 (District Cooling) - 4-pipe Fan Coil with HW Boiler |  |  | System 9 - Heating and Ventilation | System 7 (District Cooling) - VAV with Reheat
|  | System 5 (District Heating) - Packaged VAV with Reheat |  | System 9 - Heating and Ventilation |  |  | System 9 (District Heating) - Heating and Ventilation | System 7 (District Heating) - VAV with Reheat
|  |  |  | System 9 (District Heating) - Heating and Ventilation |  |  | System 9 (District Heating) - Heating and Ventilation | System 7 (Heating & Cooling) - VAV with Reheat
|  |  |  | System 10 - Heating and Ventilation |  |  | System 10 - Heating and Ventilation | System 8 - VAV with PFP Boxes
[7 empty] | System 10 - Heating and Ventilation | System 8 (District Cooling)- VAV with PFP Boxes